## TBE for Tray
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني و مربوط به موقعیت W008N
TBE/TBA FOR INSTRUMENT BULK ITEMS - W008N
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 1 از 1
9184 – 073 - 053 |  | BK | W008N | PEDCO | 110 | IN | TB | 0003 | D01
TBE FOR INSTRUMENT CABLE TRAY
ITEM | DESCRIPTION | REQUIREMENT |  |  | VENDORS
[5 empty] | TALIRAN Eng. |  | SEPCO |  | Monavar Gostar
GENERAL
1 | Quotation Reference/Date | According to vendor's proposal |  |  | PRT/8417-R1 Dated 00/10/07 |  | Proposal 4151 Date 00/10/08 |  | W018S Project, Date 00/10/07
2 | Vendor (Manufaturer) | In compliance with AVL |  |  | Yes, AVL List Submitted |  | Yes, AVL List Submitted |  | Yes
3 | Supply of 2 Years Spares Parts | 20% Spare Part |  |  | Not Submitted |  | Not Submitted |  | Not Submitted
4 | Subvendor List | In compliance with AVL |  |  | Not Submitted |  | Not Submitted |  | Not Submitted
5 | Quantity for Items | As Required |  |  | Quantity is submitted for two Wellhead |  | Item No. 5 of MTO not submitted |  | More than Required
6 | Guarantee Terms | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. Vendor shall be able to provide spares back up and support for the plant life of at least 20 years. |  |  | Not Specified |  | Not Specified |  | Not Specified
7 | Technical Exception/Deviation List | As Required |  |  | Not Submitted |  | Not Submitted |  | Not Specified
8 | Equipment Catalouge | As Required |  |  | Not Submitted |  | Submitted |  | Not Submitted
9 | Equipment Drawing | As Required |  |  | Submitted |  | Not Submitted |  | Included
10 | Reference List | Required |  |  | Submitted |  | Submitted |  | Included
CABLE TRAY , FITTING & ACCESSORIES
11 | Field Cable Tray with Safety Straight tray with cover | According to PMR |  |  | Yes |  | Yes |  | Yes
12 | Tray Material | Hot Dip Galvinized Mild Steel |  |  | Yes |  | Yes |  | Yes
13 | Cable Tray Width/Length/Height | 200mm/3m /100mm |  |  | Yes |  | Yes |  | Yes
14 | Cable Tray Thickness | 1.5 mm |  |  | Yes |  | Yes |  | Yes
15 | 90° Horizontal Bend Thickness | 1.5 mm |  |  | Yes |  | Yes |  | Yes
16 | Horizontal Bend Width/Height | 200mm Width 100mm Height |  |  | Yes |  | Yes |  | Yes
17 | Horizontal Bend Material | Hot Dip Galvinized Mild Steel |  |  | Yes |  | Yes |  | Yes
18 | Bonding Jumper Wire with Bolt & Nut | As Required |  |  | Copper Wire with 20x3mm, 300mm, M8 x 20 Bolt & Nut Dacromet - 2 set Shoe 50 |  | Not Submitted |  | Yes
19 | Bolt & Not for Tray | 1/4" by 3/4" round head galvanized |  |  | M8 x 20 - Dacromet |  | M8 x 20 - Dacromet |  | M8 x 20 - Dacromet M6 x 20 - Dacromet
20 | Bolt & Not for Support | 1/4" by 1" round head galvanized |  |  | Not Submitted |  | Not Submitted |  | Not Submitted
21 | Joint Piece (Connector) | As Required |  |  | Joint Piece with 100mm Height |  | Joint Piece with 100mm Height |  | Joint L Type with 90mm Height
22 | Rubber type sharp end protection | As Required |  |  | Not Submitted |  | Not Submitted |  | Not Submitted
PROPOSAL DOCUMENTATION
23 | Quality plan / ITP | According to the project Requirement |  |  | Submitted |  | Not Submitted |  | Not Submitted
24 | Standard certificates | According to the project Requirement |  |  | Not Submitted |  | Not Submitted |  | Not Submitted
VENDOR DOCUMENTATION
25 | VENDOR DOCUMENTATION REQUIRED AS PER MR | As Required |  |  | Not Specified |  | Not Specified |  | Not Specified
GENERAL TECHNICAL ACCEPTANCE OF QUOTATION |  |  |  |  | ACCEPTED |  | ACCEPTED |  | ACCEPTED