## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-PI-SP-0001-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0039 |  |  | Transmital Date: 09-Aug.-2021
Document Title: SPECIFICATION FOR COLOR CODING AND MARKING |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-PI-TR-0039 |  |  | Transmital Date:09-Aug.-2021
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-000-PI-SP-0001-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در بند 3.1 صقحه 5 استانداردهاي زير اضاقه شود: IPS-E-TP-100 Engineering Standard for Paints BS 5383 Material Identification of Steel, Nickel Alloy and Titanium Alloy tubes by Continuous Character Marking and Colour Coding of Steel Tubes MSS SP25 Standard marking system for valves fittings, flanges & unions مدرك Piping Material Specification |  | BK-SUR-ENG-PIP-00-01462 | 2021-09-05 | نظر کارفرمای محترم اعمال گردید.
2 | برای اقلامی که در استاندارد مربوطه کد رنگ مشخص شده؛ کد رنگ بایستی مطابق استاندارد قید گردد و موارد تکمیلی اضافه گردد. برای مثال در استاندارد ASME B16.20 در خصوص کد رنگ گسکت مشخص شده است و برای گسکت های RTJ و Rubber موارد تکمیلی قید گردد. |  | BK-SUR-ENG-PIP-00-01462 | 2021-09-05 | همانطوط که در بند 7.8.1 اشاره شد کد رنگ مربوط به گسکت های اسپرال باید طبق استاندارد ASME 16.20 باشد. در این استاندارد برای دیگر گسکت ها رنگی تعریف نشده است و لذا کد رنگ 8004 برای گسکت های RTJ در نظر گرفته شد. گسکت rubber در پروژه نداریم.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: J.mousazadeh | Signature |  |  |  | Clarified By: A.Dabiri | Signature
| Date:05-Sep.-2021 |  |  |  |  | Date: 05-Sep.-2021