## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: Data Sheets For Pig Signaler |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0888 |  |  | Transmital Date: 01 May 2022
Document Title: BK-PPL-PEDCO-320-IN-DT-0010_D01 |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0888 |  |  | Transmital Date: 01 May 2022
[5 empty] | CRS No: NISCO-CRS-BK-PPL-PEDCO-320-IN-DT-0010_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrumentation Comments
1 | electrical connection بصورت M20 x 1.5 در نظر گرفته شود. |  | 01/2294/65632 | 1401/02/27 | مطابق با جلسه ی hazop recommendation report (بند 145) ، ZS-3201 به (ZI-3201 (pig signaler indicator تبدیل گردد و نیازی به electrical connection نیست
2 | حفاظت محفظه سوئیچ ها EXD در نظر گرفته شود. |  | 01/2294/65632 | 1401/02/27 | مطابق با جلسه ی hazop recommendation report (بند 145) ، ZS-3201 به (ZI-3201 (pig signaler indicator تبدیل گردد. در آیتم 28 صفحات 5،6، 7 به ELEC. CERTIFICATE اشاره شده است ولی تعیین EXD مربوط به تجهیزات برقی می باشد که در این رویژن تمام pig signaler ها بصورت indicator می باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 18 May 2022 |  |  |  |  | Date: