## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DG-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1049 |  |  | Transmital Date: 7 Jun 2022
Document Title: Instrument Hook-up Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1049 |  |  | Transmital Date: 7 Jun 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-DG-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comment
1 | لطفا در خصوص نصب PT و FT با توجه به نوع سيال مجددا بررسي و بر اساس فاز سيالي كه بايد اندازه گيري شود، مدرك به روز رساني گردد. |  | BK-SUR-ENG-INS-01-04800 | 2022-06-21 | اصلاح گردید.
2 | با توجه به اينكه مدارك P&ID هنوز نهايي نيست مسئوليت تعداد ادوات و ادوات نصب از نظر مالي و ز ماني بر عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-04800 | 2022-06-21 | ملاحظه گردید.
3 | با توجه به اينكه، در مورد انتخاب نوع LT در مدرك مربوط به ديتاشيت داراي كامنت مي باشد. مورد بررسي و در مدرك نيز بروز رساني گردد. |  | BK-SUR-ENG-INS-01-04800 | 2022-06-21 | اصلاح گردید.
Piping Comment
4 | مراجع و استانداردها مثل IPS در مدرك ذكر گردد. |  | BK-SUR-ENG-INS-01-04800 | 2022-06-21 | در رفرنس 14 به استاندارد IPS-D-In-104 اشاره شده است.
5 | مدرك مربوط به Piping Hook-up بايستي ريفر داده شود. |  | BK-SUR-ENG-INS-01-04800 | 2022-06-21 | در رفرنس 15 به piping hook up اشاره شده است.
6 | 3- سايز انشعاب لوله قبل از اتصال به ابزار دقيق مربوطه بايستي در مدرك مشخص و مطابق IPS باشد |  | BK-SUR-ENG-INS-01-04800 | 2022-06-21 | سایز کانکشن مطابق با p&ID تصحیح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 21 Jun 2022 |  |  |  |  | Date: