## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-PY-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1051 |  |  | Transmital Date: 07/June/2022
Document Title: Plumbing & Sewage Piping Layout For Control Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-HV-TR-1051 |  |  | Transmital Date: 07/June/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-PY-0001-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در نقشه آبرسانی با توجه به وجود دوش اضطراری در اتاق باتری مطابق بند2-6-6 استاندارد IPS-G-SF-340 قطر لوله آبرسانی به 2 اینچ تغییر یابد |  | 01/2294/156737 | 1401/05/05 | انجام شد.
2 | در نقشه فاضلاب سایز 75 میلیمتر لوله های فاضلاب به 90 تغییر یابد. |  | 01/2294/156737 | 1401/05/05 | اکثریت سازندگان لوله های پوش فیت فاضلابی سایز 90 تولید نمی کنند هر جا که سایز 75 در نقشه مشخص شده جوابگوی جمع آوری فاضلاب مربوطه بوده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H.ADINEH | Signature | M.FAKHARIAN
| Date: |  |  |  |  | Date: 09/NOV/2022