## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-IN-SP-0010_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1029 |  |  | Transmital Date: 31 May 2022
Document Title: Specification For Instrument/F&G Cables |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1029 |  |  | Transmital Date: 31 May 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-000-IN-SP-0010_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بر اساس استاندار IPS-M-IN-190: Conductors for instrument signal wire shall be soft annealed copper. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | در بخش contractors مربوط به هر Type آورده شده است.
2 | اطلاعات مربوط به Overall jackets در مدرك اضافه گردد. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | مطابق خواست کارفرمای محترم اضافه شد.
3 | مورد زير در spec قيد گردد: The minimum thickness of insulation |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | مطابق خواست کارفرمای محترم اضافه شد.
4 | بر اساس استاندار IPS-M-IN-190: Insulation rating of single wires shall be not less than 600 volts. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | مطابق خواست کارفرمای محترم اضافه شد.
5 | موارد زير براي سيم هاي single pair در نظر گرفته شود: Pairs of wire shall be twisted at least 20 times per meter and have total coverage electrostatic shield with copper drain wire extending the length of the conductors. An overall jacket shall be provided for each pair. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | مطابق خواست کارفرمای محترم اضافه شد.
6 | موارد زير براي Multi conductor cable در نظر گرفته شود: Wire size should be minimum 1.0 mm2 stranded copper, and insulated. Individual pairs of wires shall have number identification. Multiple pairs shall be twisted at least 6 times per meter and shall have total coverage of electrostatic shield with 0.5 mm2 stranded copper drain wire extending the length of the conductors. An overall jacket shall be provided for the cable. An insulated communication wire should be provided within each cable. Where shields are specified for individual pairs of wires, each shield shall be insulated from other shields and from the overall cable shield. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | مطابق خواست کارفرمای محترم اضافه شد.
7 | نكته زير در ارتباط با سيگنالهاي آنالوگ در نظر گرفته شود: These wires or cables shall be enclosed in conduits or and in lugs, and should not be mixed with AC signal wiring or power wires. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19
8 | مورد زير در نظر گرفته شود: The wire or cable should have a temperature rating of 75°C as a minimum |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | اضافه شد.
9 | مورد زير براي overall jacket material در نظر گرفته شود: The overall jacket material should be moisture resistant, abrasion resistant and compatible with the environment and flame retardant specified as per IEC 60332. When cable used in emergency shutdown system, overall jacket as specified material shall be fire resistant (IEC-60331). |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | مطابق خواست کارفرمای محترم اضافه شد.
10 | اطلاعات مربوط به Fiber Optic بصورت كامل در مدرك اضافه گردد. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | کابل Fiber optic در این پروژه تعریف نشده است.
11 | اطلاعات مربوط به Data Highway/Serial Link بصورت كامل در مدرك اضافه گردد. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | کابلهای سریال و دیتا مطابق استاندارد IPS-M-IN-190 بر اساس استاندارد سازندگان تهیه خواهد شد.
12 | بخش Earthing با توجه به الزامات IPS-E-IN-190 تكميل گردد. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | کابلهای Earthing مطابق مدارک بخش برق تهیه خواهد شد.
13 | الزامات و محدوديت هاي مربوط به CONTROL ROOM WIRING در مدرك آورده شود |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | رجوع شودINSTRUMENT & CONTROL DESIGN CRITERIA به مدرک
14 | GUIDES ON SIGNALS SEPARATION در مدرك اضافه گردد. |  | BK-SUR-ENG-INS-01-04741 | 2022-06-19 | رجوع شودINSTRUMENT & CONTROL DESIGN CRITERIA به مدرک
15
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 18 Jun 2022 |  |  |  |  | Date: