## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | DT | 0002 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR TEMPERATURE GAUGE نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | NOV.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F9Z-708582
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | DT | 0002 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN |  | DT | 0002 | D02
REFERENCE DOCUMENTS :
|  | Instrument & Control System Design Criteria | [5 empty] | BK-PPL-PEDCO-320-IN-DC-0001
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0001
|  | P&ID - Condensate Pipeline (to Binak PU) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0002
|  | Piping Material Specification | [5 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Specification For Instrumentation | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Instrument Hook-Up Diagram | [5 empty] | BK-PPL-PEDCO-320-IN-DG-0002
|  | Process Basic of Design | [5 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
D02

## Notes
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0002 | D02
GENERAL NOTES:
1- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
2- S.S name plate shall be supplied for all instruments specified in this document. Following details shall be engraved on them:
• Tag Number • Range Limit • Manufacturer model and serial number
3-According to "Process Basic of Design" Document, Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C)
Minimum ambient temperature: 5 (°C)
Maximum steel surface exposed to sun: 85 (°C)
Maximum summer dry bulb: 50 (°C)
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
4- Temperature gauges shall be fully adjustable type (Every Angle).
5- Temperature gauges shall be double scale type (°C and °F).
6 - Material Test Certificate and calibration Certificate for all gauges to be submitted by Vendor.

## TG
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 | [5 empty] | BK | PPL | PEDCO | 320 | IN | DT |  | 0002 |  | D02
TEMPERATURE GAUGE
| GENERAL DATA |  | 1 |  | Tag No. |  |  | Service | [5 empty] | SEE PAGE 6
|  |  | 2 |  | P&ID |  |  | Line No./Equipment No. | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 3 |  | Piping Class |  |  | Schedule | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 4 |  | Line Size | [8 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 5 |  | Area Clacification |  |  | Phase | [5 empty] | ZONE 2, IIB T4
| PROCESS CONDITION |  | 6 |  | Fluid |  |  | Design Temperature | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 7 |  | Operating Temperature |  |  | Design Pressure |  |  |  | (°C) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 8 |  | Operating Pressure | [6 empty] | (barg) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 9 |  | Density |  |  | Viscosity (Liquid) |  |  |  | (Kg/m3) |  | SEE PAGE 6
|  |  | 10 |  | Viscosity (Vapor) |  |  | Velocity (Liquid) |  |  |  | (C.P) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 11 |  | Velocity (Vapor) | [6 empty] | (m/s) |  | SEE PAGE 6 |  |  | SEE PAGE 6
| THERMOMETER |  | 12 |  | Type | [8 empty] | Bimetal-Every Angle
|  |  | 13 |  | Instrument Range |  |  | Dial Color | [5 empty] | SEE PAGE 6 |  |  | white, non-rusting metal with black figures
|  |  | 14 |  | Dial Size |  |  | Dial Material | [5 empty] | 150 mm |  |  | Aluminum
|  |  | 15 |  | Case Material |  |  | Window | [5 empty] | SS 304 |  |  | Safety Glass (Note 1)
|  |  | 16 |  | Stem Material | [8 empty] | VTA (min SS 316/316Lmaterial )
|  |  | 17 |  | Stem Adjustable Union | [8 empty] | Required
|  |  | 18 |  | Stem Position | [8 empty] | Bottom
|  |  | 19 |  | Stem Length | [8 empty] | Suit for Well (VTA) (Note 4)
|  |  | 20 |  | Stem Diameter | [8 empty] | 6 mm
|  |  | 21 |  | Accuracy | [8 empty] | ±1% of F.S
|  |  | 22 |  | Weather Protection | [8 empty] | IP-65 as minimum-Hermitically sealed
|  |  | 23 |  | Zero Adjustement | [8 empty] | Local
| THERMOWELL (Note 2,3) |  | 24 |  | Construction Type | [8 empty] | Drilled Solid Bar Stock in Tapered Configuration
|  |  | 25 |  | Element Connection | [8 empty] | 1/2 " NPTF
|  |  | 26 |  | Size (in) |  |  | Rating (lbs) | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 27 |  | Process Connection | [8 empty] | Flanged
|  |  | 28 |  | Flange Facing | [8 empty] | SEE PAGE 6
|  |  | 29 |  | Insertion Length(U) | [6 empty] | (mm) |  | SEE PAGE 6
|  |  | 30 |  | LAG Extension (T) | [6 empty] | (mm) |  | N/A
|  |  | 31 |  | Flange Material | [8 empty] | ASTM A105
|  |  | 32 |  | Well Material | [8 empty] | S.S 316
|  |  | 33 |  | NACE Requirements (NACE MR-0175/ISO 15156) | [8 empty] | SEE PAGE 6
|  |  | 37 |  | Wake Frequency Standard | [8 empty] | Required as per ASME PTC 19.3
| PURCHASING DATA |  | 38 |  | Model |  |  | Manufacturer | [5 empty] | Will be Finalized later |  |  | Will be Finalized later
|  |  | 39 |  | Supplier |  |  | Order | [5 empty] | Will be Finalized later |  |  | Will be Finalized later
40
NOTES :
|  | VTA : VENDOR TO ADVISE |  | N/A: NOT APPLICABLE
(1) Window shall be heavy plate glass, breakage resistance and shatter proof.
(2) Thermowell wake frequency analysis (stress calculation) according to ASME Power Test Code 19.3 shall be done & submitted by vendor.
(3) Well length must suit for stem length.
(4) According to thermowell dimension, suitable length should be provided for thermometer stem.
(5) Temperature gauges shall be fully adjustable type (Every Angle).
(6) Temperature gauges shall be double scale type (°C and °F).
(7) Requirements of BK-PPL-PEDCO-320-PI-SP-0001/ BK-GNRAL-PEDCO-000-PI-SP-0008 and NACE-MR-0175/ISO 15156 shall be covered where in Piping/Pipeline Material Specification recommended.
(8) Refer to IPS-D-IN-101 for U length.
D02

## TG LIST
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN | DT |  | 002 |  |  | D02
TEMPERATURE GAUGE
Item No. | Tag No. | P&ID No. | Service | Piping Class | Line No./Equipment No. | Line Size/ Flange Facing/ Sch | Fluid/Phase | Oper./ Max. Temprature (°C) | Design Temprature (°C) | Oper./Max. Pressure (barg) | Design Pressure (barg) | Velocity (m/s) | Density (Kg/m3) (Mixed) | Viscosity (CP) (vapour/liquid) | Actual Vol. Flow (m3/h) (Gas/ Oil) | Instrument Range (°C) | Proccess. Conn. (in) | Conn. Rating | Nozzel Length. (mm) | Insertion Length (U) mm | NACE
1 | TG-3202 | BK-PPL-PEDCO-320-PR-PI-0001-03 (3/3) | Before Pig Receiver | FN05 | GAS-113-0115-FN05-8"-PT | 8"/RF/SCH 80 | GAS/GAS | 31.3/31.3 | 85 | 40 | 62 | 3.01 | 49.09/-/- | 0.01 / 0.14 | 349.8 | 0-100 | Flanged 1 1/2 RF | 600# | 162 | 200 | Yes
D02