## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0006 |  |  |  |  | EPC Contractor Tr. No. : BK-HD-PEDCO-T-1540 |  |  | Transmital Date: 24-OCT-2022
Document Title : Standard Drawing For Catch Basins |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0006-CV-T-1540 |  |  | Transmital Date: 24-OCT-2022
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0006-D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در پاسخ به ردیف 2 از Clarification (By EPC Contractor) ضمن مراجعه به صفحه 1 از 2 نقشه Catch Basin For All Areas به Top Level Manhole اشاره گردیده در صورتیکه این مدرک مربوط به Catch Basin می باشد. موضوع اصلاح نشده لذا اقدام گردد. |  | 1401-2294-296557 | 1401/08/14 | اعمال شد
2 | پاسخ گفته شده در ردیف 4 از Clarification (By EPC Contractor) مورد تایید نیست. بنابر عدم پیوستگی مناسب بین دیواره Opening و لوله با دوغاب سیمانی و همچنین تشکیل ترک های داخلی، موضوع عدم نفوذپذیری بر قوت خود باقی خواهد ماند. لذا استفاده از مصالح Sealant غیر حلال نفتی مد نظر می باشد. |  | 1401-2294-296557 | 1401/08/14
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: