## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL I/O SIGNAL LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | EL | LI | 0005 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL I/O SIGNAL LIST نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | Nov.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Jun.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-709070
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL I/O SIGNAL LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | LI | 0005 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 51
2 | X | X | [6 empty] | 52
3 | X | X | [6 empty] | 53
4 | X | X | [6 empty] | 54
5 | X | X | [6 empty] | 55
6 | X | X | [6 empty] | 56
7 | X | X | [6 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LEGEND
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL I/O SIGNAL LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | EL | LI | 0005 | D01
1. REFERENCE DOCUMENT LIST:
- I/O List for Control System "BK-GCS-PEDCO-120-IN-LI-0002"
- I/O List for ESD System "BK-GCS-PEDCO-120-IN-LI-0003"
- I/O List for F&G System "BK-GCS-PEDCO-120-IN-LI-0004"
- Wiring Diagram For Interposing Relay Panel (IRP) "BK-GCS-PEDCO-120-EL-DG-0011"
- LV Switchgear/MCC Single Line Diagram "BK-GCS-PEDCO-120-EL-SL-0002"
- Existent MV Switchgear Expansion Single Line Diagram "BK-GCS-PEDCO-120-EL-SL-0003"
- Instrument / F&G Cable List "BK-GCS-PEDCO-120-EL-LD-0001"
- Control Logic Diagram for LV Incomers & Bus Tie "BK-GCS-PEDCO-120-IN-LI-0009"
- ESD Level Hierarchy "BK-GCS-PEDCO-120-IN-DG-0003"
2. ABBREVIATION
- DI: Digital Input
- DO: Digital Output
- HW: Hard Wire
- SL: Serial Link
- CO: Close/Open
- I/O: Input / Output
- SWG: Switchgear
- TR: Transformer
- LV: Low Voltage Switchgear/MCC
- MV: Medium Voltage Switchgear
- DG: Diesel Generator
- IRP: Interposing Relay Panel
- DCS: Distributed Control System
- S.S: Selector Switch
- ATS: Automatic Transfer System
- RCP: Remote Control Panel
D01

## IRP(Process)
Control System I/O List
Item | Bus | Electrical Equipment Number | Load | Instrument Description | Description | From | To | IO Type | SIGNAL TRANSFER METHOD | Signal Tag
1 | GCS-400-NSWG-001A | P-2101A | Slug Pump A | P-2101A | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2111A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2111A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2111A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2111A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2111A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2111-A
2 | GCS-400-NSWG-001B | P-2101B | Slug Pump B | P-2101B | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2111B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2111B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2111B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2111B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2111B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2111-B
3 | GCS-400-NSWG-001A | AC-2121A | First Stage Air Cooler 21A | From 1ST Stage Gas Compressor Air Coolers (AE-2101-A) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2121A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2121A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2121A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2121A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2121A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2101-A-1
4 | GCS-400-NSWG-001A | AC-2122A | First Stage Air Cooler 22A | From 1ST Stage Gas Compressor Air Coolers (AE-2101-A) | Local/Remote Status | LV LV SWG | IRP (DCS) | DI | HW | XL-2122A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2122A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2122A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2122A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2122A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2101-A-2
5 | GCS-400-NSWG-001B | AC-2121B | First Stage Air Cooler 21B | From 1ST Stage Gas Compressor Air Coolers (AE-2101-B) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2121B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2121B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2121B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2121B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2121B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2101-B-1
6 | GCS-400-NSWG-001B | AC-2122B | First Stage Air Cooler 22B | From 1ST Stage Gas Compressor Air Coolers (AE-2101-B) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2122B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2122B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2122B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2122B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2122B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2101-B-2
7 | GCS-400-NSWG-001A | AC-2121C | First Stage Air Cooler 21C | From 1ST Stage Gas Compressor Air Coolers (AE-2101-C) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2121C
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2121C
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2121C
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2121C
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2121C
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2101-C-1
8 | GCS-400-NSWG-001A | AC-2122C | First Stage Air Cooler 22C | From 1ST Stage Gas Compressor Air Coolers (AE-2101-C) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2122C
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2122C
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2122C
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2122C
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2122C
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2101-C-2
9 | GCS-400-NSWG-001A | AC-2131A | Second Stage Air Cooler 31A | From 2ND Stage Gas Compressor Air Coolers (AE-2102-A) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2131A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2131A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2131A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2131A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2131A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2102-A-1
10 | GCS-400-NSWG-001A | AC-2132A | Second Stage Air Cooler 32A | From 2ND Stage Gas Compressor Air Coolers (AE-2102-A) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2132A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2132A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2132A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2132A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2132A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2102-A-2
11 | GCS-400-NSWG-001B | AC-2131B | Second Stage Air Cooler 31B | From 2ND Stage Gas Compressor Air Coolers (AE-2102-B) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2131B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2131B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2131B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2131B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2131B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2102-B-1
12 | GCS-400-NSWG-001B | AC-2132B | Second Stage Air Cooler 32B | From 2ND Stage Gas Compressor Air Coolers (AE-2102-C) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2132B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2132B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2132B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2132B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2132B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-AE-2102-B-2
13 | GCS-400-NSWG-001A | AC-2131C | Second Stage Air Cooler 31C | From 2ND Stage Gas Compressor Air Coolers (AE-2102-C) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2131C
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2131C
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2131C
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2131C
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2131C
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-2131C
14 | GCS-400-NSWG-001A | AC-2132C | Second Stage Air Cooler 32C | From 2ND Stage Gas Compressor Air Coolers (AE-2102-C) | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | AC-2132C
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2132C
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2132C
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2132C
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2132C
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-2132C
15 | GCS-400-NSWG-001A | P-2103A | Glycol Transfer Pump A | P-2103A | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2161A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2161A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2161A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2161A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2161A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2161-A
16 | GCS-400-NSWG-001B | P-2103B | Glycol Transfer Pump B | P-2103B | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2161B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2161B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2161B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2161B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2161B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2161-B
17 | GCS-400-NSWG-001A | P-2203A | Sump Pump A | P-2203-A | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2222A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2222A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2222A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2222A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2222A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2203-A
18 | GCS-400-NSWG-001B | P-2203B | Sump Pump B | P-2203-B | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2222B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2222B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2222B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2222B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2222B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2203-B
19 | GCS-400-NSWG-001A | P-2202A | Closed Drain Pump A | P-2202-A | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2221A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2221A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2221A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2221A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2221A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2202-A
20 | GCS-400-NSWG-001B | P-2202B | Closed Drain Pump B | P-2202-B | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2221B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2221B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2221B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2221B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2221B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2202-B
21 | GCS-400-NSWG-001A | P-2209 | Potable Water Pump | P-2209 | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2291
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2291
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2291
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2291
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2291
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2209
22 | GCS-400-NSWG-001A | P-2206 | Diesel Oil Pump | P-2206 | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2281A
[5 empty] | Running/Stop Status | LV SWG | IRP (DCS) | DI | HW | XR-2281A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2281A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2206
23 | GCS-400-NSWG-001E | P-2201A | LP Flare K.O. Drum Pump A | P-2201 A | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2251A
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2251A
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2251A
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2251A
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2251A
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-2201A
24 | GCS-400-NSWG-001E | P-2201B | LP Flare K.O. Drum Pump B | P-2201 B | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2251B
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2251B
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2251B
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2251B
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2251B
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-2201B
25 | GCS-400-NSWG-001B | P-2104 | Glycol Drain Pump | P-2104 | Local/Remote Status | LV SWG | IRP (DCS) | DI | HW | XL-2293
[5 empty] | Running Status | LV SWG | IRP (DCS) | DI | HW | XR-2293
[5 empty] | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-2293
[5 empty] | Start Command | IRP (DCS) | LV SWG | DO | HW | XSS-2293
[5 empty] | Stop Command | IRP (DCS) | LV SWG | DO | HW | XSP-2293
[5 empty] | Trip Command | IRP (ESD) | LV SWG | DO | HW | ESD-P-2104
تسهیلات
ELECTRICAL I/O SIGNAL LIST
NISOC
شماره پیمان:
9184 – 073 - 053`
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0005
D01
بسته کاری
GCS
پروژه
BK
D01
D01

## EL
Electrical System I/O List
Item | EQ. Tag No. | SIGNAL DESCRIPTION | PURPOSE | From | To | IO Type | SIGNAL TRANSFER METHOD | Signal Tag
1 | GCS-400-NSWG | 400 V SWGR-Incoming A-Q0A | Open/Close Status | LV SWG | IRP (DCS) | DI | HW | XOC-LV-Q0A
|  |  | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-LV-Q0A
2 | GCS-TR-001 | 11/0.42 KV TR-001 | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-TR-001
3 | GCS-400-NSWG | 400 V SWGR-Incoming B-Q0B | Open/Close Status | LV SWG | IRP (DCS) | DI | HW | XOC-LV-Q0B
|  |  | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-LV-Q0B
4 | GCS-TR-002 | 11/0.42 KV TR-002 | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-TR-002
5 | GCS-400-NSWG | 400 V SWGR-Bus Tie-Q0C | Open/Close Status | LV SWG | IRP (DCS) | DI | HW | XOC-LV-Q0C
|  |  | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-LV-Q0C
6 | GCS-400-NSWG | 400 V SWGR-DG C.B-Q0E | Open/Close Status | LV SWG | IRP (DCS) | DI | HW | XOC-LV-Q0E
|  |  | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-LV-Q0E
7 | GCS-400-NSWG | 400 V SWGR-DG Bus Tie-Q0D | Open/Close Status | LV SWG | IRP (DCS) | DI | HW | XOC-LV-Q0D
|  |  | Fault Status | LV SWG | IRP (DCS) | DI | HW | XF-LV-Q0D
8 | GCS-110-UPS-001 | 110 V AC UPS-001-CH01 | On/Off Status | Charger in Control Room | DCS | - | SL | XO-UPS-001-CH01
|  |  | Current Sample |  |  |  |  | XC-UPS-001-CH01
|  |  | Voltasge Sample |  |  |  |  | XV-UPS-001-CH01
|  |  | Fault Status |  | ESD | DI | HW | ESD R0-UPS-A
|  |  | Isolation Command | ESD | Charger | DO | HW | ESD 0-EL2A
|  |  | Inhibit to Boost | F&G |  | DO | HW | INB-FG-1101A
9 | GCS-110-UPS-001 | 110 V AC UPS-001-CH02 | On/Off Status | Charger in Control Room | DCS | - | SL | XO-UPS-001-CH02
|  |  | Current Sample |  |  |  |  | XC-UPS-001-CH02
|  |  | Voltasge Sample |  |  |  |  | XV-UPS-001-CH02
|  |  | Fault Status |  | ESD | DI | HW | ESD R0-UPS-B
|  |  | Isolation Command | ESD | Charger | DO | HW | ESD 0-EL2B
|  |  | Inhibit to Boost | F&G |  | DO | HW | INB-FG-1101B
10 | GCS-24-UPS-002 | 24 V DC UPS-002-CH01 | On/Off Status | Charger in Control Room | DCS | - | SL | XO-UPS-002-CH01
|  |  | Current Sample |  |  |  |  | XC-UPS-002-CH01
|  |  | Voltasge Sample |  |  |  |  | XV-UPS-002-CH01
|  |  | Fault Status |  |  |  |  | XF-UPS-002-CH01
|  |  | Isolation Command | ESD | Charger | DO | HW | ESD 0-EL3A
|  |  | Inhibit to Boost | F&G |  | DO | HW | INB-FG-1102A
11 | GCS-24-UPS-002 | 24 V DC UPS-002-CH02 | On/Off Status | Charger in Control Room | DCS | - | SL | XO-UPS-002-CH02
|  |  | Current Sample |  |  |  |  | XC-UPS-002-CH02
|  |  | Voltasge Sample |  |  |  |  | XV-UPS-002-CH02
|  |  | Fault Status |  |  |  |  | XF-UPS-002-CH02
|  |  | Isolation Command | ESD | Charger | DO | HW | ESD 0-EL3B
|  |  | Inhibit to Boost | F&G |  | DO | HW | INB-FG-1102B
12 | GCS-110-UPS-001 | 110 V AC UPS-001 | Battery Fan | F&G | Dist Panel for Battery Room | DO | HW | XBf-UPS-001
13 | GCS-110-CHG-001 | 110 V DC Charger-001-CH01 | On/Off Status | Charger in Switchgear Room | DCS | - | SL | XO-CHG-001-CH01
|  |  | Current |  |  |  |  | XC-CHG-001-CH01
|  |  | Voltasge |  |  |  |  | XV-CHG-001-CH01
|  |  | Fault Status |  |  |  |  | XF-CHG-001-CH01
|  |  | Isolation Command | IRP (ESD) | Charger | DO | HW | ESD 0-EL4A
|  |  | Inhibit to Boost | IRP (F&G) |  |  |  | INB-FG-1103A
14 | GCS-110-CHG-002 | 110 V DC Charger-001-CH02 | On/Off Status | Charger in Switchgear Room | DCS | - | SL | XO-CHG-001-CH02
|  |  | Current |  |  |  |  | XC-CHG-001-CH02
|  |  | Voltasge |  |  |  |  | XV-CHG-001-CH02
|  |  | Fault Status |  |  |  |  | XF-CHG-001-CH02
|  |  | Isolation Command | IRP (ESD) | Charger | DO | HW | ESD 0-EL4B
|  |  | Inhibit to Boost | IRP (F&G) |  |  |  | NB-FG-1103B
15 | GCS-110-UPS-001 | 110 V DC UPS-001 | Battery Fan | F&G | Dist Panel for Battery Room | DO | HW | XXXX
16 | GCS-11000-SWG-001A | 11/0.4 KV SWGR-Transformer Feeder-Q2 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001A-Q2
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001A-Q2
|  |  | Isolation Command | IRP (ESD 0) | MV SWG | DO | HW | ESD 0-EL 1A
17 | GCS-11000-SWG-001A | 11 KV SWGR-Gas Compressor-A-2101A-Q3 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001A-Q3
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001A-Q3
|  |  | Isolation Command | IRP (ESD 1A) | MV SWG | DO | HW | XOS-MV-001A-Q3
18 | GCS-11000-SWG-001A | 11 KV SWGR-Gas Compressor-C-2101C-Q4 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001A-Q4
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001A-Q4
|  |  | Isolation Command | IRP (ESD 1A) | MV SWG | DO | HW | XOS-MV-001A-Q4
19 | GCS-11000-SWG-001A | 11 KV SWGR-Spare-Q5 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001A-Q5
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001A-Q5
20 | GCS-11000-SWG-001B | 11/0.4 KV SWGR-Transformer Feeder-Q2 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001B-Q2
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001B-Q2
|  |  | Isolation Command | IRP (ESD 0) | MV SWG | DO | HW | ESD 0-EL 1B
21 | GCS-11000-SWG-001B | 11 KV SWGR-Gas Compressor-C-2101B-Q3 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001B-Q3
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001B-Q3
|  |  | Isolation Command | IRP (ESD 1A) | MV SWG | DO | HW | XOS-MV-001B-Q3
22 | GCS-11000-SWG-001B | 11/3.3 KV SWGR-Transformer Feeder-Q4 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001B-Q4
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001B-Q4
23 | GCS-11000-SWG-001B | 11 KV SWGR-Spare-Q5 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001B-Q5
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001B-Q5
24 | GCS-3300-SWG-001C | 3.3 KV SWGR-Fire Pump-Q3 | Open/Close Status | MV SWG | IRP (DCS) | DI | HW | XOC-MV-001C-Q3
|  |  | Fault Status | MV SWG | IRP (DCS) | DI | HW | XF-MV-001C-Q3
25 | GCS-400-NSWG | 400 V SWGR Auto/Manual S.S for ATS | Auto/Manual Status | LV SWG | IRP (DCS) | DI | HW | XL-ATS
26 | GCS-11000-SWG-001A | 11/0.4 KV SWGR-Transformer Feeder-Q2 | Close Status | MV SWG | RCP | AI | HW | XC-MV-001A-Q2
|  |  | Open Status | MV SWG | RCP | AI | HW | XO-MV-001A-Q2
|  |  | Breaker In Service | MV SWG | RCP | AI | HW | XI-MV-001A-Q2
|  |  | Fault Status | MV SWG | RCP | AI | HW | XF-MV-001A-Q2
|  |  | Stop Command | RCP | MV SWG | DO | HW | XSP-MV-001A-Q2
|  |  | Start Command | RCP | MV SWG | DO | HW | XSS-MV-001A-Q2
27 | GCS-11000-SWG-001B | 11/0.4 KV SWGR-Transformer Feeder-Q2 | Close Status | MV SWG | RCP | AI | HW | XC-MV-001B-Q2
|  |  | Open Status | MV SWG | RCP | AI | HW | XO-MV-001B-Q2
|  |  | Breaker In Service | MV SWG | RCP | AI | HW | XI-MV-001B-Q2
|  |  | Fault Status | MV SWG | RCP | AI | HW | XF-MV-001B-Q2
|  |  | Stop Command | RCP | MV SWG | DO | HW | XSP-MV-001B-Q2
|  |  | Start Command | RCP | MV SWG | DO | HW | XSS-MV-001B-Q2
28 | GCS-11000-SWG-001B | 11/3.3 KV SWGR-Transformer Feeder-Q4 | Close Status | MV SWG | RCP | AI | HW | XC-MV-001B-Q4
|  |  | Open Status | MV SWG | RCP | AI | HW | XO-MV-001B-Q4
|  |  | Breaker In Service | MV SWG | RCP | AI | HW | XI-MV-001B-Q4
|  |  | Fault Status | MV SWG | RCP | AI | HW | XF-MV-001B-Q4
29 | GCS-400-NSWG | 400 V SWGR-Incoming A-Q1 | Multifunction Meter | LV SWG | IRP (DCS) | DI | SL | XM-LV-IN1
30 | GCS-400-NSWG | 400 V SWGR-Incoming B-Q2 | Multifunction Meter | LV SWG | IRP (DCS) | DI | SL | XM-LV-IN2
تسهیلات
ELECTRICAL I/O SIGNAL LIST
NISOC
شماره پیمان:
9184 – 073 - 053`
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0005
D01
بسته کاری
GCS
پروژه
BK