## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0005_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1099 |  |  | Transmital Date: 20-Jun-2022
Document Title: Electrical I/O Signal List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1099 |  |  | Transmital Date: 20-Jun-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-LI-0005_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ارتباط ترانس دیوسرها با سیستم کنترل در مدرک نمایش داده شود. |  | 1401-2294-183482 | 1401-05-27 | مطابق با نوت شماره دو در مدرک تک خطی "BK-GCS-PEDCO-120-EL-SL-0002" ارتباط بین واحدهای اندازه گیری (مولتی متر) بر روی ورودیهای 1 و 2 باسیستم DCS به صورت لینک سریال و از طریق پورت ارتباطی RS482 می باشد. از اینرو موارد مذکور در مدرک Signal List نشان داده شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 05-Jul-22 |  |  |  |  | Date: