## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1107 |  |  | Transmital Date: 22-Jun-2022
Document Title: Calculation Note For Outdoor Area Lighting System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0104-EL-TR-1107 |  |  | Transmital Date: 22-Jun-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on Plot Plan Drawing and hazardous area classification layout documents. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | در صورت هرگونه تغییر این مدرک ویرایش خواهد شد.
2 | A separat table shall be added to this document and shall be compared calculated Lux with IPS-E-EL-100 standard to check the result of calculation. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
3 | The lighting calculation of new roads shall be added to document. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | باید خروجی مجددا گرفته شود.
4 | According to attached existing lighting layout, some existing towers shall be added and considered impact of these lighting fixturers in calculation. Meanwhile there is difference between this document and existing lighting layout from point of view rated power of existing flood lighting. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | با توجه به محاسبات صورت پذیرفته و همچنین استفاده از چراغ های فلورست برای تجهیزات داخلی سایت و با در نظر گرفتن سه پایه چراغ برای روشنایی محوطه، وشنایی مورد نظر اخذ شده است و همچنین در تاور های ضلع شمالی چراغی اضافه نگردید.
5 | According to latest revision of plot plan, some equipment such as fire water tanks, etc shall be shown and considered impact of these in calculation. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | در مدل جدید اضافه گردیده است.
6 | According to lighting towers locations, it seems, it is necessary to consider lighting fixturers for following locations in order to facilitate maintenance and repair activities during operation stage. : 1) Air coolers specially under air coolers 2) Flare KO. drum/Close drain and sump pumps and related walk way and stair way 3) Suction drums platform and stair ways 4) slug pums shelter and other paltform, walk way and stair way in project (If required.) |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | در نظر گرفته شد.
7 | Lighting fixturers under shelters shall be added in lighting calculation to considered impact of these lighting fixturers in calculation. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | روشنایی شلترها در مدرک روشنایی Indoor نشان داده شده است. از اینرو در صورت کسب نتیجه مطلوب بدون در نظر گرفتن چراغهای شلتر، قطعا در صورت وجود آنها نتیجه بهتری به دست خواهد آمد که با توجه به محاسبات، روشنایی مناسب مطابق با استاندارد اخذ شده است.
8 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | در صورت وجود هر گونه کامنت، متعاقبا اعمال خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 06-Jul-22 |  |  |  |  | Date: