## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0005_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1099 |  |  | Transmital Date: 20-Jun-2022
Document Title: Electrical I/O Signal List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1099 |  |  | Transmital Date: 20-Jun-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-LI-0005_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -I/O List for control system -I/O List for ESD system -P&ID document base on HAZOP study. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید.
2 | The signals between DCS (IRP) and MV/LV switchgears incomings, Coupling and outgoing feeders, AC/DC UPS, generator Control panel, Transformers alarm window, packages control panel, etc shall be added to list. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید.
3 | The signals between RCP and MV switchgear incomings, Coupling and outgoings shall be added to list. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید.
4 | Type of Output/Input signals (DO/DI/AO/AI), type of connection (Hardwire/Serial Link) and type of signals (Dry/Wet) shall be added and specified. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | با توجه به اینکه ماهیت تابلوی IRP استفاده از منابع تغذیه جدا برای کنتاکتها می باشد لذا تمامی کنتاکتها خشک بوده و کنتاکت WET استفاده نمی شود.
5 | The electrical I/O list is for signals between MV/LV switchgears (Incoming, Coupling and outgoing feeders), etc. and IRP panel, so columns "from" and "to" shall be modified. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 05-Jul-22 |  |  |  |  | Date: