## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0002-D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1168 |  |  | Transmital Date: 17-Jul-2022
Document Title: Electrical Typical Schematic Diagrams For LV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0104-EL-TR-1168 |  |  | Transmital Date: 17-Jul-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DG-0002-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه 13 از 30 در فیدر موتوری پوش استاپ اضطراری به صورت Stay Put و در ابتدای مسیر قبل از کنتاکت OL منتقل شود. (یک شستی استاپ بر روی درب استارتر کفایت می کند.) |  | 1401-2294-222997 | 1401-06-22 | مطابق با صورتجلسه پوش باتون استاپ به قبل از مسیر کنتاکت منتقل گردید. همچنین حفاظت ولتاژی و جریانی در مسیرهای متفاوت قرار گرفته است..
2 | صفحه 16 از 30: محل تغذیه بخش حفاظت ولتاژی رله MPR قبل از کنتاکتور و بعد از سوییچ فیوز نمایش داده شود. |  | 1401-2294-222997 | 1401-06-22 | اعمال گردید.
3 | کنتاکت حفاظت 27 و 47 به صورت نرمالی اپن در مسیر سرویس قرار داده شود. |  | 1401-2294-222997 | 1401-06-22 | مطابق با صورتجلسه در دفتر آن کارفرمای محترم مقرر گردید که وضعیت کنتاکت توسط سازنده مشخص گردد.
4 | صفحه 22 از 30: بند8 نامه شماره 393495 مورخ 13/11/1400 به قوت خود باقی است. در این مدار حالت تست امکان چک کردن حفاظت ها وجود ندارد |  | 1401-2294-222997 | 1401-06-22 | مطابق با صورتجلسه در دفتر آن کارفرمای محترم مقرر گردید حفاظت ولتاژی در مسیر سرویس و حفاظت جریانی هم در مسیر تست و هم در مسیر سرویس قرار گیرد که اعمال گردید.
5 | بند 25 از نامه شماره 393495 به قوت خود باقی است. |  | 1401-2294-222997 | 1401-06-22 | مطابق با بند 4 از صورتجلسه در دفتر آن کارفرمای محترم، مقرر گردید نقشه های شماتیک برای ورودیها و کوپلر از نقشه های طراحی تفصیلی حذف گردد و این مدارک توسط سازنده تهیه گردد. در فاز طراحی فقط نقشه های لاجیک برای این کلیدها تولید خواهد شد. از اینرو یک نوت اضافه گردید که در آن اشاره شده است سازنده می بایست مدارک لاجیک و دیاگرام تک خطی را ملاک خود قرار دهد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Jul-22 |  |  |  |  | Date: