## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-BK14-PEDCO-110-EL-MT-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1403 |  |  | Transmital Date: 14-Sep-2022
Document Title: MTO For Transmission Over Head Line - BK14 |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0106-EL-TR-1403 |  |  | Transmital Date: 14-Sep-2022
[5 empty] | CRS No: PEDCO-CRS-BK-BK14-PEDCO-110-EL-MT-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مبنای محاسبات کالای ارتینگ دکل ها و همچنین شیوه اجرای آن ارائه نشده است. مقتضی است مدارک مرتبط ارائه گردد. |  | 1401-2294-249368 | 1401-07-13 | 1. همانگونه كه مستحضريد ارتينگ برج هاي خطوط انتقال بر اساس استاندارد توانير (نشريه شماره 409 معاونت نظارت راهبردي) و به صورت كانترپويز به نحوي اجرا ميگردد كه دو يا چهار پايه برج بر اساس مقاومت مخصوص خاك محل برج، زمين ميگردد. برآورد صورت گرفته براي ارتينگ بر همين اساس و با فرض سختگيرانه ترين شرايط انجام و در بندهاي 20 الي 24 ارائه شده است. شيوه اجرايي نيز بر اساس استاندارد مذكور و در شكل هاي 2-6 الي 2-8 استاندارد ارائه شده است. 2. ملاحظه گرديد.
| در خصوص ساختار کلی مدرک نظر خاصی مطرح نیست. بدیهی است مسئولیت متراژ، تعداد و تطابق آن با نیازمندی های پروژه و استانداردهای مربوطه بر عهده آن شرکت می باشد. |  | 1401-2294-249368 | 1401-07-13 | با توجه به اينكه مدرك مجزايي جهت MTO تجهيزات گنتري محل انشعاب و گنتري سر چاهي وجود ندارد، لذا MTO اين تجهيزات نيز در ادامه MTO تجهيزات خط اضافه گرديد. (بر اساس بند 6 صورتجلسه مورخ 1401/08/10,11 در محل سالن جلسات طرح 28 مخزن ناحيه گچساران و همچنین صورتجلسه بازدید مورخ 1401/08/24 در محل سالن جلسات کمپ بینک)
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 28-Sep-22 |  |  |  |  | Date: