## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE TRANSMITTER/SWITCH
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0005 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR TEMPERATURE TRANSMITTER/SWITCH نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | NOV.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-708926
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE TRANSMITTER/SWITCH
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0005 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 |  | X | [6 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE TRANSMITTER/SWITCH
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0005 | D01
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002
D01

## NOTES
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE TRANSMITTER/SWITCH
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 7
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0005 | D01
GENERAL NOTES:
1- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as the minimum and shall be verified by vendor.
2 - Vendor is responsible for the selection of Materials suitable for the specified working conditions.
3 - All lines below 4", shall be expanded to 4" to be suitable for thermowell installation.
4- Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
• Tag Number • Range Limit • Service • Manufacture Model
5- All transmitters shall have output short circuit & reverse polarity protection.
6- Sunshade to be considered for all transmitters.
7- All transmitters shall have a none-volatile EEprom memory to be used for storing the configuration data and sensor linearization data. This data must be retained in the transmitter to be functional upon power up.
8- Vendor shall identify and detail any deviation from the present instrument datasheet.
9- All transmitters shall be equipped with internal diagnostics software.
10- Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB for Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
D01

## TT
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE TRANSMITTER/SWITCH
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 7
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN | DT | 0005 | D01
TEMPERATURE TRANSMITTER
GENERAL DATA |  |  | 1 | Tag No. | [7 empty] | SEE PAGE 6 & 7
|  |  | 2 | P&ID |  |  |  | Service |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 3 | Piping Class |  |  |  | Line No. |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 4 | Line Size |  |  |  | Schedule |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 5 | Area Clacification | [7 empty] | Zone 2- IIB T4
|  |  |  | RFI Protection |  |  |  | Tropicalisation |  |  |  | NEEDED |  | NEEDED
PROCESS CONDITION |  |  | 6 | Fluid |  |  |  | Phase |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 7 | Operating Temperature |  |  |  | Design Temperature |  |  | (°C) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 8 | Operating Pressure |  |  |  | Design Pressure |  |  | (barg) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 9 | Density (Winter) |  |  |  | Density (Summer) |  |  | (Kg/m3) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 10 | Viscosity (Winter) |  |  |  | Viscosity (Summer) |  |  | (C.P) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 11 | Velocity | [6 empty] | (m/s) | SEE PAGE 6 & 7
TRANSMITTER |  |  | 12 | Thermoelement Type | [7 empty] | RTD
|  |  | 13 | Housing Material | [7 empty] | Die-Cast Aluminum
|  |  | 14 | Power Supply | [7 empty] | 24 VDC, Loop Powered
|  |  | 15 | Output Signal |  |  |  | Communication Protocol |  |  |  | 4-20 mA |  | HART (SMART TYPE)
|  |  | 16 | Instrument Range |  |  |  | Calibrated Range |  |  |  | SEE PAGE 6 & 7 |  | VTA
|  |  | 17 | Integral Digital Indicator |  |  |  | Scale |  |  |  | Required |  | Calibrated in Engineering unit
|  |  | 18 | Accuracy | [7 empty] | +/- 0.1 % Calibrated Span
|  |  | 19 | Burn Out Direction | [7 empty] | Up Scale
|  |  | 20 | Ingress Protection |  |  |  | Electrical Certification |  |  |  | IP-65 as minimum |  | EEx ia, IIB T4
|  |  | 21 | Electrical Connection |  |  |  | Cable Gland |  |  |  | ISO M20 x 1.5 |  | Required
|  |  | 22 | Mounting | [7 empty] | Compact With Element
|  |  | 23 | Calibration Range |  |  |  | Write Protection |  |  |  | VTA |  | SEE PAGE 6 & 7 (Note 3)
HEAD |  |  | 24 | Head Type |  |  |  | Material |  |  |  | Top Mounted-Screwed |  | Die-cast aluminum with baked vinyl finish.
|  |  | 25 | Terminal Block | [7 empty] | With 4 Terminal Wires
|  |  | 26 | Weather Protection |  |  |  | Electrical Certification |  |  |  | IP-65 as minimum |  | EEx ia,IIB T4
|  |  | 27 | Electrical Connection |  |  |  | Cable Gland |  |  |  | ISO M20 |  | Required
|  |  | 28 | Nipple Size | [7 empty] | 1/2 " NPT
TEMPERATURE ELEMENT |  |  | 29 | Type | [7 empty] | RTD
|  |  | 30 | Resistance |  |  |  | Wire Size |  |  |  | 100 ohms at 0 degree Celsius. |  | VTA
|  |  | 31 | Single / Double |  |  |  | No. of Wires |  |  |  | SEE PAGE 6 & 7 |  | 3 Wires
|  |  | 32 | Sheath Material |  |  |  | Sheath OD |  |  |  | 316 S.S |  | VTA
|  |  | 33 | Stem Length |  |  |  | Leads |  |  |  | To Match Thermowell |  | VTA
|  |  | 34 | Mounting Thread |  |  |  | Sealing |  |  |  | 1/2 " NPT |  | Hermetical
|  |  | 35 | Accuracy | [7 empty] | Class A as per IEC 60751
THERMOWELL |  |  | 36 | Construction Type | [7 empty] | Drilled Bar Stock in Tapered Configuration
|  |  | 37 | Element Connection | [7 empty] | 1/2" NPT
|  |  | 38 | Size (in) |  |  |  | Rating (lbs) |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 39 | Process Connection |  |  |  | Flange Facing / Finish (μm) |  |  |  | Flanged |  | SEE PAGE 6 & 7
|  |  | 40 | Insertion Length (U) mm |  |  |  | LAG Extension (T) mm |  |  |  | SEE PAGE 6 & 7 |  | VTA
|  |  | 41 | Flange Material |  |  |  | Well Material |  |  |  | 316L S.S |  | 316L S.S
|  |  | 42 | Wake Frequency Standard | [7 empty] | Required as per ASME PTC 19.3
|  |  | 43 | NACE Requirements | [7 empty] | SEE PAGE 6 & 7 (Note 1)
44
PURCHASING DATA |  |  | 45 | Model |  |  |  | Manufacturer |  |  |  | will be finalized later |  | will be finalized later
|  |  | 46 | Supplier |  |  |  | Order |  |  |  | will be finalized later |  | will be finalized later
47
NOTES :
VTA : Vendor to Advise VTC : Vendor to Confirm N/A: Not Applicable
(1) Thermowell wake frequency analysis (stress calculation) according to ASME Power Test
Code 19.3 shall be done & submitted by vendor.
(2) The element length shall be compatible with well length.
(3) The transmitters which shall be write protected are identified by note 2 in sheet 6. (Also see note 2 in sheet 7)
D01

## TT LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE TRANSMITTER/SWITCH
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO |  | 120 | IN | DT |  | 0005 |  | D01
TEMPERATURE TRANSMITTER LIST
Rev. | Item No. | Tag No. | P&ID No. | Service | Piping Class | Line/Equipment No. | Line Size | Fluid | Phase | Operating Temperature (°C) | Design Temperature (°C) | Operating Pressure (barg) | Design Pressure (barg) | Density (Kg/m3) | Viscosity (CP) | Velocity (m/s) | Instrument Range (°C) | Calibration Range (°C) | Projection Length (mm) | Size (in) | Rating /Facing | Max Insertion Length (U) mm | Nace
D01 MODIFIED | 1 | TIT-2102 | BK-GCS-PEDCO-120-PR-PI-0002-D04 | TO INLET K.O. DRUM | AN07 | GAS-111-0101-AN07-6"-PT | 6" | PROCESS GAS | GAS | 46.11/26.67 | 85 | 7.5 | 9 | 6.66 | 0.011 | 14.68 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D01 MODIFIED | 2 | TIT-2104 | BK-GCS-PEDCO-120-PR-PI-0003-D04 | TO SLUG CATCHER | FN05 | GAS-111-0001-FN05-8"-PT | 8" | PROCESS GAS | GAS | 32/15.5 | 85 | 7.5 | 9 | 6.21 | 0.011 | 9.9 | VTA | 0-65 | 162 NOTE 1 | 1 1/2" | 600/RF | 300 | YES
D01 DELETED | 3 | TIT-2111 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | GAS | AN07 | GAS-111-0012-AN07-14"-PT | 14" | PROCESS GAS | GAS | 32/15.5 | 85 | 5.5 | 9 | 6.21 | 0.011 | 9.9 | VTA | 0-65 | 135 NOTE 1 | 1 1/2" | 300/RF | 350 | YES
D01 MODIFIED | 4 | TIT-2112 | BK-GCS-PEDCO-120-PR-PI-0005-D04 | INLET K.O. DRUM INPUT | AN07 | GAS-111-0005-AN07-10"-PT | 10" | PROCESS GAS | GAS | 37.17/19.23 | 85 | 5.3 | 9 | 6.16 | - | 15.79 | VTA | 0-80 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D01 MODIFIED | 5 | TIT-2121A | BK-GCS-PEDCO-120-PR-PI-0007-D04 (1 of 3) | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101A) | AN05 | GAS-111-0031A-AN05-8"-ET | 8" | PROCESS GAS | GAS | 36.78/18.88 | 85 | 4.9 | FV/9 | 5.77 | 0.011 | 12.92 | VTA | 0-80 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D01 MODIFIED | 6 | TIT-2124A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0007-D04 (1 of 3) | TO 1ST STAGE AIR COOLER (AE-2101A) | CN05 | GAS-111-0036A-CN05-6"-NP | 6" | PROCESS GAS | GAS | 124.8/113.1 | 155 | 19 | 22 | 15.38 | 0.011 | 19.05 | VTA | 0-250 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D01 MODIFIED | 7 | TIT-2121B | BK-GCS-PEDCO-120-PR-PI-0007-D04 (2 of 3) | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101B) | AN05 | GAS-111-0031B-AN05-8"-ET | 8" | PROCESS GAS | GAS | 36.78/18.88 | 85 | 4.9 | FV/9 | 5.77 | 0.011 | 12.92 | VTA | 0-80 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D01 MODIFIED | 8 | TIT-2124B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0007-D04 (2 of 3) | TO 1ST STAGE AIR COOLER (AE-2101B) | CN05 | GAS-111-0036B-CN05-6"-NP | 6" | PROCESS GAS | GAS | 124.8/113.1 | 155 | 19 | 22 | 15.38 | 0.011 | 19.05 | VTA | 0-250 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D01 MODIFIED | 9 | TIT-2121C | BK-GCS-PEDCO-120-PR-PI-0007-D04 (3 of 3) | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101C) | AN05 | GAS-111-0031C-AN05-8"-ET | 8" | PROCESS GAS | GAS | 36.78/18.88 | 85 | 4.9 | FV/9 | 5.77 | 0.011 | 12.92 | VTA | 0-80 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D01 MODIFIED | 10 | TIT-2124C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0007-D04 (3 of 3) | TO 1ST STAGE AIR COOLER (AE-2101C) | CN05 | GAS-111-0036C-CN05-6"-NP | 6" | PROCESS GAS | GAS | 124.8/113.1 | 155 | 19 | 22 | 15.38 | 0.011 | 19.05 | VTA | 0-250 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D01 MODIFIED | 11 | TIT-2126A | BK-GCS-PEDCO-120-PR-PI-0008-D04 (1 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-A) | CS00 | GAS-111-0037A-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.28 | 0.011 | 7.06 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D01 MODIFIED | 12 | TIT-2125A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0008-D04 (1 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-A) | CS00 | GAS-111-0037A-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.28 | 0.011 | 7.06 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D01 MODIFIED | 13 | TIT-2126B | BK-GCS-PEDCO-120-PR-PI-0008-D04 (2 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-B) | CS00 | GAS-111-0037B-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.28 | 0.011 | 7.06 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D01 MODIFIED | 14 | TIT-2125B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0008-D04 (2 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-B) | CS00 | GAS-111-0037B-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.28 | 0.011 | 7.06 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D01 MODIFIED | 15 | TIT-2126C | BK-GCS-PEDCO-120-PR-PI-0008-D04 (3 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-C) | CS00 | GAS-111-0037C-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.28 | 0.011 | 7.06 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D01 MODIFIED | 16 | TIT-2125C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0008-D04 (3 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-C) | CS00 | GAS-111-0037C-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.28 | 0.01 | 7.06 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D01 MODIFIED | 17 | TIT-2131A | BK-GCS-PEDCO-120-PR-PI-0010-D04 (1 of 3) | FROM 2ND STAGE GAS COMP. SUCTION DRUM (V-2102A) | CN05 | GAS-111-0044A-CN05-6"-ET | 6" | PROCESS GAS | GAS | 59.88 | 115.4 | 18.1 | FV/22 | 18.08 | 0.01 | 7.14 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D01 MODIFIED | 18 | TIT-2134A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0010-D04 (1 of 3) | TO 2ND STAGE AIR COOLER (AE-2102A) | FN05 | GAS-111-0051A-FN05-6"-IS | 6" | PROCESS GAS | GAS | 142.3/149.5 | 175 | 54.8 | 62 | 42.92 | 0.01 | 3 | VTA | 0-300 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | YES
D01 MODIFIED | 19 | TIT-2131B | BK-GCS-PEDCO-120-PR-PI-0010-D04 (2 of 3) | FROM 2ND STAGE GAS COMP. SUCTION DRUM (V-2102B) | CN05 | GAS-111-0044B-CN05-6"-ET | 6" | PROCESS GAS | GAS | 59.88 | 115.4 | 18.1 | FV/22 | 18.08 | 0.01 | 7.14 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D01 MODIFIED | 20 | TIT-2134B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0010-D04 (2 of 3) | TO 2ND STAGE AIR COOLER (AE-2102B) | FN05 | GAS-111-0051B-FN05-6"-IS | 6" | PROCESS GAS | GAS | 142.3/149.5 | 175 | 54.8 | 62 | 42.92 | 0.01 | 3 | VTA | 0-300 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | YES
D01 MODIFIED | 21 | TIT-2131C | BK-GCS-PEDCO-120-PR-PI-0010-D04 (3 of 3) | FROM 2ND STAGE GAS COMP. SUCTION DRUM (V-2102C) | CN05 | GAS-111-0044C-CN05-6"-ET | 6" | PROCESS GAS | GAS | 59.88 | 115.4 | 18.1 | FV/22 | 18.08 | 0.01 | 7.14 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D01 MODIFIED | 22 | TIT-2134C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0010-D04 (3 of 3) | TO 2ND STAGE AIR COOLER (AE-2102C) | FN05 | GAS-111-0051C-FN05-6"-IS | 6" | PROCESS GAS | GAS | 142.3/149.5 | 175 | 54.8 | 62 | 42.92 | 0.01 | 3 | VTA | 0-300 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | YES
D01 MODIFIED | 23 | TIT-2135A | BK-GCS-PEDCO-120-PR-PI-0011-D04 (1 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-A) | FS00 | GAS-111-0058A-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 130 | 54.1 | F.V/62 | 59.63 | - | 2.16 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D01 MODIFIED | 24 | TIT-2136A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0011-D04 (1 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-A) | FS00 | GAS-111-0058A-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 130 | 54.1 | F.V/62 | 59.63 | - | 2.16 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D01 MODIFIED | 25 | TIT-2135B | BK-GCS-PEDCO-120-PR-PI-0011-D04 (2 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-B) | FS00 | GAS-111-0058B-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 130 | 54.1 | F.V/62 | 59.63 | - | 2.16 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D01 MODIFIED | 26 | TIT-2136B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0011-D04 (2 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-B) | FS00 | GAS-111-0058B-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 130 | 54.1 | F.V/62 | 59.63 | - | 2.16 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D01 MODIFIED | 27 | TIT-2135C | BK-GCS-PEDCO-120-PR-PI-0011-D04 (3 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-C) | FS00 | GAS-111-0058C-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 130 | 54.1 | F.V/62 | 59.63 | - | 2.16 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D01 MODIFIED | 28 | TIT-2136C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0011-D04 (3 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-C) | FS00 | GAS-111-0058C-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 130 | 54.1 | F.V/62 | 59.63 | - | 2.16 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D01 ADDED | 29 | TT-2211 | BK-GCS-PEDCO-120-PR-PI-0016-D04 | NITROGEN RECEIVER OUTLET | AN01 | NIT-112-0024-AN01-2"-PT | 2" | NITROGEN | GAS | 60 | 85 | 8 | 12.5 | 8.65 | 0.019 | 0.42 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 200 (NOTE 3 IN GENERAL NOTES) | NO
D01 MODIFIED | 30 | TIT-2271 | BK-GCS-PEDCO-120-PR-PI-0022-D04 | FUEL GAS K.O. DRUM OUTLET | AN07 | FLG-112-0110-AN07-2"-PT | 2" | FUEL GAS | GAS | 36.7 | 85 | 4.9 | F.V/9 | 5.96 | 0.01 | 50.8 | VTA | 0-80 | 162 NOTE 1 | 1 1/2" | 300/RF | 200 (NOTE 3 IN GENERAL NOTES) | YES
NOTES:
(1) Projection Length (mm) will be finallized by piping department.
(2) Transmitters shall be of the smart transmitter type with HART communication protocol, except those connected to the ESD/HIPPS/FGS system that will be preferably of conventional electronic type. If smart type transmitters are selected for ESD application they shall be configured as “write protected”.
D01