## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0014_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0750 |  |  | Transmital Date: 27 Mar 2022
Document Title: Data Sheets For Corrosion Coupon/ Probe |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0750 |  |  | Transmital Date: 27 Mar 2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-NISOC-120-IN-DT-0014_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comments
1 | به نام و شماره مدرک مرجع برای Environmental Conditions اشاره گردد. |  | 1401-2294-27197 | 1401/01/28 | مرجع برای Environmental Conditions مدرک Process Basis Of Design با شماره مدرک BK-GNRAL-PEDCO-000-PR-DB-0001 می باشد که در رفرنس ها به آن اشاره شده. همچنین در Note 10 اضافه شد.
2 | ردیف مربوط به Wetted Part Material اضافه گردد. |  | 1401-2294-27197 | 1401/01/28 | متریال COUPON MATRIAL و ACCESS FITTING همگی معادل متریال LINE/EQUIPMENT در نظر گرفته شده که خوردگی واقعی PIPE یا Vessel را بسنجد. با این وجود برای Coupon ها این آیتم در سطر 49 اضافه شد. در مورد Probe ها این آیتم بصورت عمومی در سطر 30 مشخص شده است.
3 | به متریال Tag Plate اشاره ای نشده. ای ردیف اضافه گردد. |  | 1401-2294-27197 | 1401/01/28 | در General Note 12 اضافه شد.
4 | شماره خطوط مطابق آخرین ویرایش مدرک P&ID مورد بازنگری و موارد متناقض اصلاح گردد. |  | 1401-2294-27197 | 1401/01/28 | انجام شد.
5 | نوع پراب خوردگی تعیین گردد. |  | 1401-2294-27197 | 1401/01/28 | انجام شد.
6 | در صفحه 8 مدرک: شماره تگ های مربوط به پراب های خوردگی نادرست بوده و می بایست اصلاح گردند. |  | 1401-2294-27197 | 1401/01/28 | اصلاح شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 17 Apr 2022 |  |  |  |  | Date: