## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0005 |  |  |  |  | EPC Contractor Tr. No. : BK-HD-PEDCO-T-1515 |  |  | Transmital Date: 19-OCT-2022
Document Title : Standard Drawing For Manhole |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-CV-T-1515 |  |  | Transmital Date: 19-OCT-2022
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0005-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در پاسخ به ردیف 4 از Clarification به آگاهی می رساند که دلایل گفته شده در Reply Sheet قانع کننده نمی باشد. همانگونه که در Comment NISOC به موضوع ایمنی اشاره گردید، چنانچه محصول ورودی به منهول از نوع Oily و با تلاطم باشد خطر وقوع اشتعال بسیار زیاد خواهد بود. بتابراین برای اینگونه منهول ها مطلوب است لوله ورودی مطابق طرح پیشنهادی (نامه شماره 210047) باشد. افزون بر آن طرح آن پیمانکار (ورود لوله مایتر به منهول) هم استاندارد نبوده و هم اینکه با اشکالات اجرایی مواجه خواهد شد. لذا اصلاح گردد. |  | 1401-2294-296586 | 2022-11-05 | اعمال شد
2 | پاسخ گفته شده در ردیف 6 از Clarification (By EPC Contractor) مورد تایید نیست. بنابر عدم پیوستگی مناسب بین دیواره Opening و لوله با دوغاب گروت سیمانی و همچنین تشکیل ترک های داخلی، موضوع عدم نفوذپذیری بر قوت خود باقی خواهد ماند. لذا استفاده از مصالح Sealant غیر حلال نفتی مد نظر می باشد. |  | 1401-2294-296586 | 2022-11-05 | اعمال شد
3 | تایپ آرماتور اشاره شده در Manhole For All Areas مطابق با ردیف 7 از بخش Notes اصلاح گردد. |  | 1401-2294-296586 | 2022-11-05 | اعمال شد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: