## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0873 |  |  | Transmital Date: 27-Apr-2022
Document Title: Calculation Note For Indoor Area Lighting System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0873 |  |  | Transmital Date: 27-Apr-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on architectural detail drawing for control, existing switchgear buildings/Shelters and hazardous area classification layout documents. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | نقشه معماری تمامی ساختمانها به روز گردید و نقشه های جدید مبنای محاسبات می باشد.
2 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09
2-1 | A separate table shall be added to this document and shall be compared calculated Lux with IPS-E-EL-100 standard to check the result of calculation. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | اعمال گردید.
2-2 | The calculation shall be rechecked and modified from point of view the dimensions of the rooms/Shelters and value of standard lux for example for control room. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | اعمال گردید.
2-3 | Lighting calculation for transformer shelter shall be added. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | محاسبات اتاق ترانس در نظر گرفته شد.
3 | Type of lighting fixtures shall be selected base on hazardous area classification. (Gas compressor shelter and chemical injection packages & storage shelter) |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | چراغ های شلتر ها در محدوده ناحیه فرآیندی Explosion Proof در نظر گرفته شده است.
4 | Workplane/Value Chart shall be added to output reports for each room to check Emin/Emax. For example for corridor its about 0.1 that shall be modified in order to achieve uniform lighting. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | اعمال گردید.
5 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | در صورت وجود هر گونه کامنت، متعاقبا اعمال خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 09-May-22 |  |  |  |  | Date: