## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
ELECTRICAL LOAD LIST OF WELL PADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 10
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | EL | LI | 0001 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL LOAD LIST OF WELL PADS نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | Nov.2022 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | Apr.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | Mar.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Jan.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-707418
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Revision
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
ELECTRICAL LOAD LIST OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 10
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 110 | EL | LI | 0001 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 51
2 | X | X | X |  | X |  |  |  | 52
3 | X | [7 empty] | 53
4 | X | [7 empty] | 54
5 | X | X | X |  | X |  |  |  | 55
6 | X | X | X |  | X |  |  |  | 56
7 | X | X | X |  | X |  |  |  | 57
8 | X | X | X |  | X |  |  |  | 58
9 | X | X | X |  | X |  |  |  | 59
10 | X | X | X |  | X |  |  |  | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## Abb
Service Type:
N : Normal Load
E : Emergency Load
Load Duty:
C : Continuous Load
I : Intermitant Load
S : Stand By Load
LR/FL: Loacked Rotor / Full Load Current
Load Type:
M: Motor
F: Non-Motor
Definition of API Factor
1.25 for Motor Power < 22kW,
1.15 for Motor Power between, 22kW and 55kW
1.1 for Motor Power > 55kW
Height derating factor can be determined as follows if no manufacturer data is available:
Height Above Sea Level | Height Factor
< 1000 m | 1
1000 < Height < 1500 m | 0.97
1500 m > | 0.94
Coolant (Cooling) Factor will be finilized by Electromotors Vendor Datd and before that will be considered :0.88
Feeder Type:
F1: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for I<63A Feeders
F2: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for 63A=<I<100A Feeders
F3: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for 100A=<I Feeders
F4: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for I<63A Feeders
F5: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for 63A=<I<100A Feeders
F6: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for 100A=<I Feeders
F7: Simple 2-Pole MCCB Feeder for Feeding Single Phase Loads (Ph+N or 2-Ph)
M1: Direct on Line Motor Starter Feeders for P < 4kW (Switch Fuse + Contactor + Bimetal + R/L Signaling)
M2: Direct on Line Motor Starter Feeders for 4kW ≤ P < 18.5kW (Switch Fuse + Contactor + Bimetal + R/L Signaling + R/L Ammeter)
M3: Direct on Line Motor Starter Feeders for 18.5kW ≤ P <30 (Switch Fuse + Contactor + Bimetal + R/L Signaling + R/L Ammeter + (49, 50G, Phase Control))
M4: Direct on Line Motor Starter Feeders for 30kW ≤ P (Switch Fuse + Contactor + Overload CT + R/L Signaling + R/L Ammeter + Motor Protection Relay (49, 50G, Phase Control))
تسهیلات
ELECTRICAL LOAD LIST OF WELL PADS
شماره صفحه: 3 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0001
D03
بسته کاری
SSGRL
پروژه
BK

## Calculation
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
ELECTRICAL LOAD LIST OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 10
9184 – 073 - 053 |  |  | BK | SSGRL | PEDCO | 110 | EL | LI | 0001 | D03
| 1. Mechanical Power (KW): |  | Mechanical Power for Motors = BHP(KW) x API Factor / (Cooling Factor x Height Factor)
| 2. Rated Power(KW): |  | Rated Power = The Nearest Size of The Equipment to Mechanical Power of Motors
| 3. Load Factor(%): |  | Load Factor = (BHP/Rated Power) x 100
| 4. Normal Operation(A): |  | Normal Operation (A) = Rated Power / (Sqrt(3) x Nominal Voltage x cosØ)
| 5. Starting Current(A): |  | Starting Current(A) = (LR/LF) x Normal Current
6. Electrical Power Demand (KW):
Electrical Absorbed Power Demand (KW) = BHP(KW) x Diversity Factor / Efficiency
Electrical Absorbed Power Demand (KW) = Rated Power(KW) x Diversity Factor / Efficiency
7. Electrical Reactive Power Demand (KVAR):
Electrical Reactive Power Demand (KVAR) = Electrical Absorbed Power Demand (KW) x Tangent(Ø
For "Electrical Demand" calculation, following "Diversity Factors" has been considered (based on peak loads):
Continous: 100% Diversity factor.
Intermittent: Normally less than 12 hours/day, As generaly 75%
Standby: Spare/Backup drives or systems, As generaly 10% or biggest standby load (which is bigger)

## BK-12
Load List of Well-12
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (KVA) | Feeder Type
1 | D03 | Well12-400-NSWG-001 | 1-PU-40 (W12) | Electrical Submersible Pump & Equipment | N | C | 1 | 3 | 0.4 | F | VFD | - | - | - | - | - | 75 | 90 | 85 | 100 | 1 | 141.5074 | 83.3333 | 51.6454 | 98.0392 | F3
2 | D03 | Well12-400-NSWG-001 | 1-PU-30 (W12) | Auxiliary Submersible Pump | N | C | 1 | 3 | 0.4 | M | DOL | 3 | - | - | - | - | 3 | 81 | 85 | 100 | 7 | 6.2892 | 3.7037 | 2.2953 | 4.3573 | M1
3 | D00 | Well12-400-NSWG-001 | Well12-110-CHG-001 | 110VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 0.3 | 0.18592 | 0.35294 | F1
4 | D00 | Well12-400-NSWG-001 | Well12-110-CHG-002 | 110VDC Charger 2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 3 | 1.8592 | 3.5294 | F1
5 | D03 | Well12-400-NSWG-001 | Well12-DP01 | Distribution Panel for Switchgear & Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 20.5556 | 12.7392 | 24.183 | F1
6 | D00 | Well12-400-NSWG-001 | Well12-DP02 | Distribution Panel for Guard House | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 6 | 90 | 85 | 100 | 1 | 11.3206 | 6.6667 | 4.1316 | 7.8431 | F1
7 | D03 | Well12-400-NSWG-001 | Well12-DP03 | Distribution Panel for Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 90 | 85 | 100 | 1 | 0 | 0 | 0 | 0 | F1
8 | D02 | Well12-400-NSWG-001 | Well12-WS01 | Welding Socket | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 37 | 100 | 85 | 100 | 1 | 62.8293 | 27.75 | 17.1979 | 32.6471 | F2
Well12-400-NSWG-001
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 117.2593 | 72.6708 | 27.75 | 17.1979 | 0.3 | 0.18592
[13 empty] | Well12-400-NSWG-001 | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 145.0093 | 89.8687 | 170.5991 | 0.85
[19 empty] | Peak Load |  | 145.3093 | 90.0546 | 170.9521 | 0.85
[13 empty] | 37 | 3 | 22.9305 | 1.8592 |  |  | Peak Load With 20% Spare (KVA) |  |  |  | 205.1425
1. According to basic document, there is a normal switchgear for well-12 which will be fed from 250 KVA transformer 11/0.42 KV.
2. Power factor will be calculated while all capacitor banks are out of service.
تسهیلات
ELECTRICAL LOAD LIST OF WELL PADS
شماره صفحه: 5 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0001
D03
بسته کاری
SSGRL
پروژه
BK

## BK-15
Load List of Well-15
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (KVA) | Feeder Type
1 | D03 | Well15-400-NSWG-001 | 1-PU-40 (W15) | Electrical Submersible Pump & Equipment | N | C | 1 | 3 | 0.4 | F | VFD | - | - | - | - | - | 75 | 90 | 85 | 100 | 1 | 141.5074 | 83.3333 | 51.6454 | 98.0392 | F3
2 | D03 | Well15-400-NSWG-001 | 1-PU-30 (W15) | Auxiliary Submersible Pump | N | C | 1 | 3 | 0.4 | M | DOL | 3 | - | - | - | - | 3 | 81 | 85 | 100 | 7 | 6.2892 | 3.7037 | 2.2953 | 4.3573 | M1
3 | D00 | Well15-400-NSWG-001 | Well15-110-CHG-001 | 110VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 0.3 | 0.18592 | 0.35294 | F1
4 | D00 | Well15-400-NSWG-001 | Well15-110-CHG-002 | 110VDC Charger 2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 3 | 1.8592 | 3.5294 | F1
5 | D03 | Well15-400-NSWG-001 | Well15-DP01 | Distribution Panel for Switchgear & Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 20.5556 | 12.7392 | 24.183 | F1
6 | D00 | Well15-400-NSWG-001 | Well15-DP02 | Distribution Panel for Guard House | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 6 | 90 | 85 | 100 | 1 | 11.3206 | 6.6667 | 4.1316 | 7.8431 | F1
7 | D03 | Well15-400-NSWG-001 | Well15-DP03 | Distribution Panel for Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 90 | 85 | 100 | 1 | 0 | 0 | 0 | 0 | F1
8 | D02 | Well15-400-NSWG-001 | Well15-WS01 | Welding Socket | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 37 | 100 | 85 | 100 | 1 | 62.8293 | 27.75 | 17.1979 | 32.6471 | F2
Well15-400-NSWG-001
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 117.2593 | 72.6708 | 27.75 | 17.1979 | 0.3 | 0.18592
[13 empty] | Well15-400-NSWG-001 | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 145.0093 | 89.8687 | 170.5991 | 0.85
[19 empty] | Peak Load |  | 145.3093 | 90.0546 | 170.9521 | 0.85
[13 empty] | 37 | 3 | 22.9305 | 1.8592 |  |  | Peak Load With 20% Spare (KVA) |  |  |  | 205.1425
1. According to basic document, there is a normal switchgear for well-15 which will be fed from 250 KVA transformer 11/0.42 KV.
2. Power factor will be calculated while all capacitor banks are out of service.
تسهیلات
ELECTRICAL LOAD LIST OF WELL PADS
شماره صفحه: 6 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0001
D03
بسته کاری
SSGRL
پروژه
BK

## BK-05
Load List of Well-05
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (KVA) | Feeder Type
1 | D03 | Well05-400-NSWG-001 | 1-PU-40 (W05) | Electrical Submersible Pump & Equipment | N | C | 1 | 3 | 0.4 | F | VFD | - | - | - | - | - | 75 | 90 | 85 | 100 | 1 | 141.5074 | 83.3333 | 51.6454 | 98.0392 | F3
2 | D03 | Well05-400-NSWG-001 | 1-PU-30 (W05) | Auxiliary Submersible Pump | N | C | 1 | 3 | 0.4 | M | DOL | 3 | - | - | - | - | 3 | 81 | 85 | 100 | 7 | 6.2892 | 3.7037 | 2.2953 | 4.3573 | M1
3 | D00 | Well05-400-NSWG-001 | Well05-110-CHG-001 | 110VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 0.3 | 0.18592 | 0.35294 | F1
4 | D00 | Well05-400-NSWG-001 | Well05-110-CHG-002 | 110VDC Charger 2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 3 | 1.8592 | 3.5294 | F1
5 | D03 | Well05-400-NSWG-001 | Well05-DP01 | Distribution Panel for Switchgear & Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 20.5556 | 12.7392 | 24.183 | F1
6 | D00 | Well05-400-NSWG-001 | Well05-DP02 | Distribution Panel for Guard House | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 6 | 90 | 85 | 100 | 1 | 11.3206 | 6.6667 | 4.1316 | 7.8431 | F1
7 | D03 | Well05-400-NSWG-001 | Well05-DP03 | Distribution Panel for Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 90 | 85 | 100 | 1 | 0 | 0 | 0 | 0 | F1
8 | D02 | Well05-400-NSWG-001 | Well05-WS01 | Welding Socket | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 37 | 100 | 85 | 100 | 1 | 62.8293 | 27.75 | 17.1979 | 32.6471 | F2
Well05-400-NSWG-001
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 117.2593 | 72.6708 | 27.75 | 17.1979 | 0.3 | 0.18592
[13 empty] | Well05-400-NSWG-001A | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 145.0093 | 89.8687 | 170.5991 | 0.85
[19 empty] | Peak Load |  | 145.3093 | 90.0546 | 170.9521 | 0.85
[13 empty] | 37 | 3 | 22.9305 | 1.8592 |  |  | Peak Load With 20% Spare (KVA) |  |  |  | 205.1425
1. According to basic document, there is a normal switchgear for well-05 which will be fed from 250 KVA transformer 11/0.42 KV.
2. Power factor will be calculated while all capacitor banks are out of service.
تسهیلات
ELECTRICAL LOAD LIST OF WELL PADS
شماره صفحه: 7 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0001
D03
بسته کاری
SSGRL
پروژه
BK

## WH-007
Load List of Well-007
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (KVA) | Feeder Type
1 | D03 | Well007-400-NSWG-001 | 1-PU-40 (W007) | Electrical Submersible Pump & Equipment | N | C | 1 | 3 | 0.4 | F | VFD | - | - | - | - | - | 75 | 90 | 85 | 100 | 1 | 141.5074 | 83.3333 | 51.6454 | 98.0392 | F3
2 | D03 | Well007-400-NSWG-001 | 1-PU-30 (W007) | Auxiliary Submersible Pump | N | C | 1 | 3 | 0.4 | M | DOL | 3 | - | - | - | - | 3 | 81 | 85 | 100 | 7 | 6.2892 | 3.7037 | 2.2953 | 4.3573 | M1
3 | D00 | Well007-400-NSWG-001 | Well007-110-CHG-001 | 110VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 0.3 | 0.18592 | 0.35294 | F1
4 | D00 | Well007-400-NSWG-001 | Well007-110-CHG-002 | 110VDC Charger 2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 3 | 1.8592 | 3.5294 | F1
5 | D03 | Well007-400-NSWG-001 | Well007-DP01 | Distribution Panel for Switchgear & Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 20.5556 | 12.7392 | 24.183 | F1
6 | D00 | Well007-400-NSWG-001 | Well007-DP02 | Distribution Panel for Guard House | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 6 | 90 | 85 | 100 | 1 | 11.3206 | 6.6667 | 4.1316 | 7.8431 | F1
7 | D03 | Well007-400-NSWG-001 | Well007-DP03 | Distribution Panel for Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 90 | 85 | 100 | 1 | 0 | 0 | 0 | 0 | F1
8 | D02 | Well007-400-NSWG-001 | Well007-WS01 | Welding Socket | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 37 | 100 | 85 | 100 | 1 | 62.8293 | 27.75 | 17.1979 | 32.6471 | F2
Well007-400-NSWG-001
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 117.2593 | 72.6708 | 27.75 | 17.1979 | 0.3 | 0.18592
[13 empty] | Well007-400-NSWG-001 | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 145.0093 | 89.8687 | 170.5991 | 0.85
[19 empty] | Peak Load |  | 145.3093 | 90.0546 | 170.9521 | 0.85
[13 empty] | 37 | 3 | 22.9305 | 1.8592 |  |  | Peak Load With 20% Spare (KVA) |  |  |  | 205.1425
1. According to basic document, there is a normal switchgear for well007 which will be fed from 250 KVA transformer 11/0.42 KV.
2. Power factor will be calculated while all capacitor banks are out of service.
تسهیلات
ELECTRICAL LOAD LIST OF WELL PADS
شماره صفحه: 8 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0001
D03
بسته کاری
SSGRL
پروژه
BK

## WH-046
Load List of Well-046
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (KVA) | Feeder Type
1 | D03 | Well046-400-NSWG-001 | 1-PU-40 (W046) | Electrical Submersible Pump & Equipment | N | C | 1 | 3 | 0.4 | F | VFD | - | - | - | - | - | 75 | 90 | 85 | 100 | 1 | 141.5074 | 83.3333 | 51.6454 | 98.0392 | F3
2 | D03 | Well046-400-NSWG-001 | 1-PU-30 (W046) | Auxiliary Submersible Pump | N | C | 1 | 3 | 0.4 | M | DOL | 3 | - | - | - | - | 3 | 81 | 85 | 100 | 7 | 6.2892 | 3.7037 | 2.2953 | 4.3573 | M1
3 | D00 | Well046-400-NSWG-001 | Well046-110-CHG-001 | 110VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 0.3 | 0.18592 | 0.35294 | F1
4 | D00 | Well046-400-NSWG-001 | Well046-110-CHG-002 | 110VDC Charger 2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 3 | 1.8592 | 3.5294 | F1
5 | D03 | Well046-400-NSWG-001 | Well046-DP01 | Distribution Panel for Switchgear & Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 20.5556 | 12.7392 | 24.183 | F1
6 | D00 | Well046-400-NSWG-001 | Well046-DP02 | Distribution Panel for Guard House | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 6 | 90 | 85 | 100 | 1 | 11.3206 | 6.6667 | 4.1316 | 7.8431 | F1
7 | D03 | Well046-400-NSWG-001 | Well046-DP03 | Distribution Panel for Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 90 | 85 | 100 | 1 | 0 | 0 | 0 | 0 | F1
8 | D02 | Well046-400-NSWG-001 | Well046-WS01 | Welding Socket | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 37 | 100 | 85 | 100 | 1 | 62.8293 | 27.75 | 17.1979 | 32.6471 | F2
Well046-400-NSWG-001
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 117.2593 | 72.6708 | 27.75 | 17.1979 | 0.3 | 0.18592
[13 empty] | Well046-400-NSWG-001 | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 145.0093 | 89.8687 | 170.5991 | 0.85
[19 empty] | Peak Load |  | 145.3093 | 90.0546 | 170.9521 | 0.85
[13 empty] | 37 | 3 | 22.9305 | 1.8592 |  |  | Peak Load With 20% Spare (KVA) |  |  |  | 205.1425
1. According to basic document, there is a normal switchgear for well-046 which will be fed from 250 KVA transformer 11/0.42 KV.
2. Power factor will be calculated while all capacitor banks are out of service.
تسهیلات
ELECTRICAL LOAD LIST OF WELL PADS
شماره صفحه :9 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0001
D03
بسته کاری
SSGRL
پروژه
BK

## BK-14
Load List of Well-14
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (KVA) | Feeder Type
1 | D03 | Well14-400-NSWG-001 | 1-PU-40 (W14) | Electrical Submersible Pump & Equipment | N | C | 1 | 3 | 0.4 | F | VFD | - | - | - | - | - | 75 | 90 | 85 | 100 | 1 | 141.5074 | 83.3333 | 51.6454 | 98.0392 | F3
2 | D03 | Well14-400-NSWG-001 | 1-PU-30 (W14) | Auxiliary Submersible Pump | N | C | 1 | 3 | 0.4 | M | DOL | 3 | - | - | - | - | 3 | 81 | 85 | 100 | 7 | 6.2892 | 3.7037 | 2.2953 | 4.3573 | M1
3 | D00 | Well14-400-NSWG-001 | Well14-110-CHG-001 | 110VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 0.3 | 0.18592 | 0.35294 | F1
4 | D00 | Well14-400-NSWG-001 | Well14-110-CHG-002 | 110VDC Charger 2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 3 | 100 | 85 | 100 | 1 | 5.0943 | 3 | 1.8592 | 3.5294 | F1
5 | D03 | Well14-400-NSWG-001 | Well14-DP01 | Distribution Panel for Switchgear & Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 20.5556 | 12.7392 | 24.183 | F1
6 | D00 | Well14-400-NSWG-001 | Well14-DP02 | Distribution Panel for Guard House | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 6 | 90 | 85 | 100 | 1 | 11.3206 | 6.6667 | 4.1316 | 7.8431 | F1
7 | D03 | Well14-400-NSWG-001 | Well14-DP03 | Distribution Panel for Outdoor Area | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 90 | 85 | 100 | 1 | 0 | 0 | 0 | 0 | F1
8 | D02 | Well14-400-NSWG-001 | Well14-WS01 | Welding Socket | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 37 | 100 | 85 | 100 | 1 | 62.8293 | 27.75 | 17.1979 | 32.6471 | F2
Well14-400-NSWG-001
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 117.2593 | 72.6708 | 27.75 | 17.1979 | 0.3 | 0.18592
[13 empty] | Well14-400-NSWG-001 | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 145.0093 | 89.8687 | 170.5991 | 0.85
[19 empty] | Peak Load |  | 145.3093 | 90.0546 | 170.9521 | 0.85
[13 empty] | 37 | 3 | 22.9305 | 1.8592 |  |  | Peak Load With 20% Spare (KVA) |  |  |  | 205.1425
1. According to basic document, there is a normal switchgear for well-14 which will be fed from 250 KVA transformer 33/0.42 KV.
2. Power factor will be calculated while all capacitor banks are out of service.
تسهیلات
ELECTRICAL LOAD LIST OF WELL PADS
شماره صفحه: 10 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0001
D03
بسته کاری
SSGRL
پروژه
BK