## Cover
NISOC |  |  | افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوري بینک
CABLE SCHEDULE FOR TELECOM EQUIPMENT
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 3
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | TE | LI | 0003 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
CABLE SCHEDULE FOR TELECOM EQUIPMENT نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | Nov .2022 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | Sep .2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | June .2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-709093
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوري بینک
CABLE SCHEDULE FOR TELECOM EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 3
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | TE | LI | 0003 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 51
2 | X | X | X | [5 empty] | 52
3 | X | X | [6 empty] | 53
4 | [8 empty] | 54
5 | [8 empty] | 55
6 | [8 empty] | 56
7 | [8 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## TECHNICAL
|  |  | FROM |  |  | TO |  |  | SIGNAL | CABLE DETAIL
Item | Rev. | Cable Tag No. | EQUIPMENT TAG No. | LOCATION | EQUIPMENT DESCRIPTION | EQUIPMENT DESCRIPTION | LOCATION | CABLE CONNECTOR/ GLAND SIZE |  | SIZE | DESCRIPTION | ESTIMATED LENGTH (m) | DRUM
Telephone Multipair Cable Between New Control Building and Exist Telephone MDF at exist TELECOM ROON
1 | D01 | MDF-01-T-01 | MDF-01 | GCS Control Building(new) | NEW TELEPHONE MDF | MDF-02 | EXISTTELECOM MDF AT Exist CCB | M20 | Analouge Telephone | 50X2X0.8 mm | CU/PVC/(SC)/CFC/SWA (OUTDOOR) | 60
Telephon Cable Between New Control Building and Field Area
2 | D01 | GCS-TJB-TC-01 | MDF-01 | GCS Control Building(new) | TELEPHONE SET | CGS-TJB-01 | GCS Field Area | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/LS (OUTDOOR) | 300
3 | D01 | GCS-TJB-TC-02 | MDF-01 | GCS Control Building(new) | TELEPHONE SET | CGS-TJB-02 | GCS Field Area | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/LS (OUTDOOR) | 250
4 | D01 | GCS-TJB-TC-03 | MDF-01 | GCS Control Building(new) | TELEPHONE SET | CGS-TJB-03 | GCS Field Area | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/LS (OUTDOOR) | 350
5 | D01 | GCS-TJB-TC-04 | MDF-01 | GCS Control Building(new) | TELEPHONE SET | CGS-TJB-04 | GCS Field Area | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/LS (OUTDOOR) | 400
6 | D01 | GCS-TJB-TC-05 | MDF-01 | GCS Control Building(new) | TELEPHONE SET | CGS-TJB-05 | GCS Field Area | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/LS (OUTDOOR) | 250
POWER Cable Between UPS Distribution Panel AND Field Area(For Flasher of Analouge Telephone)
7 | D01 | GCS-PJB-PC-01 | UPS | GCS Control Building(new) | UPS Panel | CGS-PJB-01 | Telephone PowerJB | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC/LS | 300
8 | D01 | GCS-PJB-PC-02 | UPS | GCS Control Building(new) | UPS Panel | CGS-PJB-02 | Telephone PowerJB | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC/LS | 250
9 | D01 | GCS-PJB-PC-03 | UPS | GCS Control Building(new) | UPS Panel | CGS-PJB-03 | Telephone PowerJB | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC/LS | 350
10 | D01 | GCS-PJB-PC-04 | UPS | GCS Control Building(new) | UPS Panel | CGS-PJB-04 | Telephone PowerJB | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC/LS | 400
11 | D01 | GCS-PJB-PC-05 | UPS | GCS Control Building(new) | UPS Panel | CGS-PJB-05 | Telephone PowerJB | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC/LS | 250
Telephon Cable Between New Control Building and Hotline Telephone
12 | D01 | GCS-HJB-TC-01 | MDF-01 | GCS Control Building(new) | TELEPHONE MDF | GCS-HJB-01 | Hotline Telephone JB | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/PVC/LS (OUTDOOR) | 350
13 | D01 | GCS-HJB-TC-02 | MDF-01 | GCS Control Building(new) | TELEPHONE MDF | GCS-HJB-02 | Hotline Telephone JB | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/PVC/LS (OUTDOOR) | 400
14 | D01 | GCS-HJB-TC-03 | MDF-01 | GCS Control Building(new) | TELEPHONE MDF | GCS-HJB-03 | Hotline Telephone JB | M20 | Analouge Telephone | 5X2X0.8mm | CU/PVC/(SC)/SWA/PVC/LS (OUTDOOR) | 250
Telephon Cable Between New Control Building and Electrical Building
15 | D01 | GCS-TJB-TC-01 | MDF-01 | GCS Control Building(new) | TELEPHONE MDF | CGS-TJB-01 | GCS Field Area | M20 | Analouge Telephone | 2X2X0.8 mm | CU/PVC/(SC)/SWA/PVC (OUTDOOR) | 60
16 | D01 | GCS-PJB-PC-01 | UPS | GCS Control Building(new) | UPS Panel | CGS-PJB-01 | Telephone PowerJB | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC | 60
17 | D01 | GCS-TJB-TC-05 | MDF-01 | GCS Control Building(new) | TELEPHONE MDF | TSO-01 | Telephone Socket | M20 | Analouge Telephone | 2X2X0.8mm | CU/PVC/(SC)/SWA/PVC (OUTDOOR) | 100
LS:Lead Sheath
TC : TELEPHONE CABLE
PC : POWER CCABLE
تسهیلات
CABLE SCHEDULE FOR TELECOM EQUIPMENT
شماره صفحه: 3 از 3
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
TE
LI
0003
D02
بسته کاری
GCS
پروژه
BK