## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1307 |  |  | Transmital Date: 8/24/2022
Document Title: P&ID - Gas Compression Inlet Gas Pipeline (Binak) |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1307 |  |  | Transmital Date: 8/24/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0002_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به خطرات ارسال گاز H2S به فضای آزاد، هدف از در نظر گرفتن انشعاب زیر می باید مشخص گردد. در صورت استفاده به منظور PURGE توضیحات اصلاح گردد. GAS-111-0018-AN07-2"-PT (START UP VENT TO SAFE AREA) |  | 1401-2294-281080 | 1401/08/03 | خط مذکور به منظور PURG خط لوله بینک در نظر گرفته شده است. در صورتی که عملیات PURG با گاز بی اثر انجام شود از نشعاب فوق استفاده خواهد شد. لازم به ذکر است تخلیه سیال هیدروکربنی خط لوله بینک یک انشعاب به شبکه فلر نیز در نظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021