## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0015 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1308 |  |  | Transmital Date: 8/24/2022
Document Title: P&ID - Instrument & Plant Air System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1308 |  |  | Transmital Date: 8/24/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0015_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | توصیه ردیف 86 از مدرک "HAZOP Report for Compressor Station" مد نظر قرار گیرد. |  | 1401-2294-283491 | 1401/08/07 | اعمال گردید.
2 | شیر PSV-2201 بر اساس Fire Case سایز شده و برای آن می باید یدک در نظر گرفته شود مطابق اسناد پیمان عمل شود. |  | 1401-2294-283491 | 1401/08/07 | با توجه به اینکه در Fire Case در واحد هوای ابزار دقیق کلیه واحد فرآیندی Shut Down می شود و تا راه اندازی دوباره سایت امکان کالیبره و نصب مجدد PSV وجود دارد لذا از منظر این پیمانکار در نظر گرفتن یک شیر ایمنی خللی در فرآیند ایستگاه ایجاد نمی نماید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: