## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0011 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1308 |  |  | Transmital Date: 8/24/2022
Document Title: P&ID - 2nd Stage Gas Compression Air Coolers |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1308 |  |  | Transmital Date: 8/24/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PI-0011_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | HAZOP Recommendation شماره 38 در خصوص تطابق با داده برگ، اعمال نشده است. |  | BK-SUR-ENG-PCS-01-05636 | 2022-09-12 | اعمال گردید.
2 | نقطه نظر پیشین: با توجه به عدم ارائه محاسبات Thermal برای تجهیز Air cooler و نهایی نشدن تعداد فن ها، امکان تایید نهایی این مدرک تا ارائه محاسبات، امکان پذیر نمی باشد. |  | BK-SUR-ENG-PCS-01-05636 | 2022-09-12 | در آخرین ویرایش دیتاشیت Air Cooler محاسبات ترمال و مشخصات کولر هوایی ارایه گردیده است.
3 | ابزاردقيق: بصورت عمومي براي تمامي دياگرام ها، تمامي شير هاي ESD كه با سطح 1 و صفر فعال مي شوند partial stroke در نظر گرفته شود. |  | BK-SUR-ENG-PCS-01-05636 | 2022-09-12 | نوت شماره 14 در PI-0003 در همه صفحات تکرار خواهد شد.
4 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-01-05636 | 2022-09-12 | اعمال می گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: