## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0023 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1309 |  |  | Transmital Date: 8/24/2022
Document Title: P&ID - Diesel Oil System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1309 |  |  | Transmital Date: 8/24/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0023_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق با ردیف شماره 118 از مدرک HAZOP REPORT FOR COMPRESSOR STATION لازم است مطالعات HAZOP مد نظر قرار گیرد. |  | 1401-2294-285752 | 1401/08/07 | در ویرایش قبلی مدرک اعمال شده است.
2 | می بایست همراه ویرایش بعد محاسبات مربوط به سایزینگ TSV-2281A/B ارایه گردد. |  | 1401-2294-285752 | 1401/08/07 | طبق بند 9.3 استاندارد IPS-E-450 شیرهای TSV سایز نمی شوند. آنها معمولاً برمبناي حداقل اندازه مجاز وصل شدن به لوله كشي براي كاربري خاص انتخاب ميشوند .
3 | ابعاد V-2206 مورد بررسی قرار گیرد. |  | 1401-2294-285752 | 1401/08/07 | طبق آخرین توافقات ابعاد این مخزن مطابق با ابعاد محاسبات پایه در نظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: