## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-PY-0006_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1008 |  |  | Transmital Date: 28-May-2022
Document Title: Area Electrical Cable Route & Section Layout of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1008 |  |  | Transmital Date: 28-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-PY-0006_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به احتمال عبور ماشین آلات سنگین از روی مسیر کابل در سکشن 07 لازم است که جهت مسیر این داکت بانک در نظر گرفته شود. |  | 1401-2294-118236 | 1401-04-05 | قسمتی از مسیر کابل که احتمال عبور ماشن آلات سنگین را دارد، توسط داکت بانک در نظر گرفته شده است که با توجه به تغییر در مسیر کابل، سکشن شماره 14 می باشد.
2 | با توجه به نقطه نظرات این امور بر روی مدرک محاسبات روشنایی ، مقتضی است پس از اصلاح مدرک روشنایی و تغییر جانمایی پایه ها این مدرک نیز بر این اساس اصلاح شود. |  | 1401-2294-118236 | 1401-04-05 | با توجه به شرح کار پروژه تعداد دو عدد پایه روشنایی وجود دارد که برای محوطه سرچاهی کفایت می کند. بر همین اساس مدرک روشنایی به شماره BK-SSGRL-PEDCO-110-EL-PY-0003 تولید شده است
3 | تاورهای روشنایی می بایست به گونه ای جانمایی گردند که مانعی جهت عبور و مرور ماشینهای حفاری و استقرار دکل برای تعمیرات ایجاد ننمایند. |  | 1401-2294-118236 | 1401-04-05 | بر اساس جلسه ای که با حضور کارشناسان شرکت پتروایران برگزار گردید، پایه های روشنایی به گونه ای مستقر گردید که در مسیر عبور ماشین آلات نباشد. بر همین اساس مدرک روشنایی به شماره BK-SSGRL-PEDCO-110-EL-PY-0003 تولید شده است
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Jun-22 |  |  |  |  | Date: