## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 38
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0006 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-708927
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 38
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0006 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 | X | X | [6 empty] | 74
11 | X | X | [6 empty] | 75
12 | X | X | [6 empty] | 76
13 | X | X | [6 empty] | 77
14 | X | X | [6 empty] | 78
15 | X | X | [6 empty] | 79
16 | X | X | [6 empty] | 80
17 | X | X | [6 empty] | 81
18 | X | X | [6 empty] | 82
19 | X | X | [6 empty] | 83
20 | X | X | [6 empty] | 84
21 | X | X | [6 empty] | 85
22 | X | X | [6 empty] | 86
23 | X | X | [6 empty] | 87
24 | X | X | [6 empty] | 88
25 | X | X | [6 empty] | 89
26 | X | X | [6 empty] | 90
27 | X | X | [6 empty] | 91
28 | X | X | [6 empty] | 92
29 | X | X | [6 empty] | 93
30 | X | X | [6 empty] | 94
31 | X | X | [6 empty] | 95
32 | X | X | [6 empty] | 96
33 | X | X | [6 empty] | 97
34 | X | X | [6 empty] | 98
35 | X | X | [6 empty] | 99
36 | X | X | [6 empty] | 100
37 | X | X | [6 empty] | 101
38 | X | X | [6 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 38
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0006 | D01
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002
D01

## Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 38
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0006 | D01
GENERAL NOTES:
1- Wetted part shall be in according to NACE MR-0175/ISO 15156.
2- The torque tube connection with the displacer chamber shall be flanged.
3- All transmitters shall be equipped with internal diagnostics software.
4- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as the minimum and shall be verified by vendor.
5- A material certificate to EN 10204: 2004 type 3.1 shall be provided for each process wetted part.
6- Any pressure bearing welds shall be subject to 100% radiography inspection by qualified welding NDT inspectors.
7- All transmitters shall have output short circuit & reverse polarity protection.
8- The transmitter digital electronics shall have a non-volatile EEPROM memory to be used for storing the configuration data of sensor.
9- Material Test Certificates and Calibration shall submit for each Level Transmitter by vendor.
10- Sunshade to be considered for all electronic parts.
11- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
12- Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
13- Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
• Tag Number • Range Limit • Service • Manufacture Model
D01

## LIT-2111
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 5 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2111
|  | 2 | Service | [8 empty] | Slug Catcher Drum
|  | 3 | Location | [8 empty] | V-2104
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 3)
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 694.9 Kg/m3 |  |  |  |  | 8.35 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 9 barg |  |  |  |  | 5.5 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 32 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.010 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | C.S.
|  | 14 | Body/Cage Rating | [8 empty] | 300#
|  | 15 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 16 | - | [8 empty] | -
|  | 17 | Flange Material | [8 empty] | C.S.
|  | 18 | Length of Center To Center | [8 empty] | 3048 mm (120”) (Note1)
|  | 19 | Case Mounting | [8 empty] | VTA
|  | 20 | Rotatable Head | [8 empty] | Yes
|  | 21 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Side Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2112
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 6 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2112
|  | 2 | Service | [8 empty] | Slug Catcher Drum
|  | 3 | Location | [8 empty] | V-2104
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 3)
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 694.9 Kg/m3 |  |  |  |  | 8.35 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 9 barg |  |  |  |  | 5.5 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 32 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.010 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | C.S.
|  | 14 | Body/Cage Rating | [8 empty] | 300#
|  | 15 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 16 | - | [8 empty] | -
|  | 17 | Flange Material | [8 empty] | C.S.
|  | 18 | Length of Center To Center | [8 empty] | 3048mm (120”) (Note1)
|  | 19 | Case Mounting | [8 empty] | VTA
|  | 20 | Rotatable Head | [8 empty] | Yes
|  | 21 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Side Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2116
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 7 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2116
|  | 2 | Service | [8 empty] | Gas Compression Inlet Knock Out Drum
|  | 3 | Location | [8 empty] | V-2105
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0005
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.6 Kg/m3 |  |  |  |  | 5.96 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 9 barg |  |  |  |  | 5.3 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 37.17 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.011 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | C.S.
|  | 14 | Body/Cage Rating | [8 empty] | 300#
|  | 15 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 16 | - | [8 empty] | -
|  | 17 | Flange Material | [8 empty] | C.S.
|  | 18 | Length of Center To Center | [8 empty] | 813 mm (32"), (Note1)
|  | 19 | Case Mounting | [8 empty] | VTA
|  | 20 | Rotatable Head | [8 empty] | Yes
|  | 21 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Side Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2117
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 8 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2117
|  | 2 | Service | [8 empty] | Gas Compression Inlet Knock Out Drum
|  | 3 | Location | [8 empty] | V-2105
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.6 Kg/m3 |  |  |  |  | 5.96 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 9 barg |  |  |  |  | 5.3 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 37.17 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.011 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32"), (Note1)
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Ingress Protection | [8 empty] | IP65
|  | 37 | Mounting Location | [8 empty] | Side Mounted
|  | 38 | Connection Size & Location | [8 empty] | VTA
|  | 39 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 40 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 41 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 42 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 43 | Zero/Span Adjusment | [8 empty] | VTA
|  | 44 | Termination Type | [8 empty] | Screw terminal
|  | 45 | Case Material | [8 empty] | VTA
OPTIONS |  | 46 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 47 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 48 | Compliance Code | [8 empty] | -
|  | 49 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 50 | Manufacturer | [8 empty] | VTA
|  | 51 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2118
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 9 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2118
|  | 2 | Service | [8 empty] | Gas Compression Inlet Knock Out Drum
|  | 3 | Location | [8 empty] | V-2105
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0005-D04
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.6 Kg/m3 |  |  |  |  | 5.96.16 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 5.1
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 36.92
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.68 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 356 mm (14")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-250 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2119
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 10 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2119
|  | 2 | Service | [8 empty] | Gas Compression Inlet Knock Out Drum
|  | 3 | Location | [8 empty] | V-2105
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0005
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 998.2 Kg/m3 |  |  |  |  | 6.16 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 9 barg |  |  |  |  | 5.3 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 37.17 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.68 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | C.S.
|  | 14 | Body/Cage Rating | [8 empty] | 300#
|  | 15 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 16 | - | [8 empty] | -
|  | 17 | Flange Material | [8 empty] | C.S.
|  | 18 | Length of Center To Center | [8 empty] | 356 mm (14") (Note1)
|  | 19 | Case Mounting | [8 empty] | VTA
|  | 20 | Rotatable Head | [8 empty] | Yes
|  | 21 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Side Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2121A
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 11 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2121A
|  | 2 | Service | [8 empty] | 1st Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2101-A
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D04 (1 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 36.78 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2122A
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 12 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2122A
|  | 2 | Service | [8 empty] | 1st Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2101-A
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D04 (1 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 36.78 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2121B
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 13 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2121B
|  | 2 | Service | [8 empty] | 1st Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2101-B
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 36.78 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2122B
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 14 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2122B
|  | 2 | Service | [8 empty] | 1st Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2101-B
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 36.78 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2121C
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 15 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2121C
|  | 2 | Service | [8 empty] | 1st Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2101-C
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D04 (3 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 36.78 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0No.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2122C
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 16 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2122C
|  | 2 | Service | [8 empty] | 1st Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2101-C
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D04 (3 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 36.78 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2131A
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 17 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2131A
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2102-A
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D04 (1 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 829.1 Kg/m3 |  |  |  |  | 18.08 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/22 barg |  |  |  |  | 18.1 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 115.4 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2132A
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 18 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2132A
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2102-A
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D04 (1 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 829.1 Kg/m3 |  |  |  |  | 18.08 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/22 barg |  |  |  |  | 18.1 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 115.4 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2131B
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 19 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2131B
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2102-B
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 829.1 Kg/m3 |  |  |  |  | 18.08 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/22 barg |  |  |  |  | 18.1 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 115.4 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2132B
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 20 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2132B
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2102-B
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 829.1 Kg/m3 |  |  |  |  | 18.08 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/22 barg |  |  |  |  | 18.1 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 115.4 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2131C
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 21 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2131C
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2102-C
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D04 (3 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 829.1 Kg/m3 |  |  |  |  | 18.08 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/22 barg |  |  |  |  | 18.1 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 115.4 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2132C
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 22 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2132C
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Suction Drums
|  | 3 | Location | [8 empty] | V-2102-C
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D04 (3 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 829.1 Kg/m3 |  |  |  |  | 18.08 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/22 barg |  |  |  |  | 18.1 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 115.4 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.44 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2141
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 23 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2141
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Discharge Drum
|  | 3 | Location | [8 empty] | V-2103
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0012-D04
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 982 Kg/m3 |  |  |  |  | 59.17 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/62 barg |  |  |  |  | 53.90 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 130 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.49 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2142
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 24 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2142
|  | 2 | Service | [8 empty] | 2nd Stage Gas Compression Discharge Drum
|  | 3 | Location | [8 empty] | V-2103
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0012-D04
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 982 Kg/m3 |  |  |  |  | 59.17 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/62 barg |  |  |  |  | 53.90 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 130 °C |  |  |  |  | 60 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.49 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2221
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 25 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2221
|  | 2 | Service | [8 empty] | Close Drain Drum
|  | 3 | Location | [8 empty] | V-2202
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0017
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 979.6 Kg/m3 |  |  |  |  | 1.85 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 5.5 barg |  |  |  |  | 0.5 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 60 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.45 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | C.S.
|  | 14 | Body/Cage Rating | [8 empty] | 300#
|  | 15 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 16 | - | [8 empty] | -
|  | 17 | Flange Material | [8 empty] | C.S.
|  | 18 | Length of Center To Center | [8 empty] | 2438 mm (96”) (Note1)
|  | 19 | Case Mounting | [8 empty] | VTA
|  | 20 | Rotatable Head | [8 empty] | Yes
|  | 21 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Side Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2222
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 26 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2222
|  | 2 | Service | [8 empty] | Close Drain Drum
|  | 3 | Location | [8 empty] | V-2202
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0017
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 979.6 Kg/m3 |  |  |  |  | 1.85 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 5.5 barg |  |  |  |  | 0.5 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 60 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.45 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | C.S.
|  | 14 | Body/Cage Rating | [8 empty] | 300#
|  | 15 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 16 | - | [8 empty] | -
|  | 17 | Flange Material | [8 empty] | C.S.
|  | 18 | Length of Center To Center | [8 empty] | 813 mm (32"), (Note1)
|  | 19 | Case Mounting | [8 empty] | VTA
|  | 20 | Rotatable Head | [8 empty] | Yes
|  | 21 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Side Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2223A
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 27 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE - TOP MOUNTED)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2223A
|  | 2 | Service | [8 empty] | LP FLARE K.O. DRUM AND CLOSED DRAIN DRUM SUMP
|  | 3 | Location | [8 empty] | SU-2201
|  | 4 | Mounting Type | [8 empty] | Internal
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0017
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 979.6 Kg/m3 |  |  |  |  | 1.85 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 5.5 barg |  |  |  |  | 0.5 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 60 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.45 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | N.A.
|  | 14 | Body/Cage Rating | [8 empty] | N.A.
|  | 15 | Connection Size & Location | [8 empty] | N.A.
|  | 16 | - | [8 empty] | N.A.
|  | 17 | Flange Material | [8 empty] | N.A.
|  | 18 | Length of Center To Center | [8 empty] | N.A.
|  | 19 | Case Mounting | [8 empty] | N.A.
|  | 20 | Rotatable Head | [8 empty] | N.A.
|  | 21 | Orientation | [8 empty] | N.A.
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Top Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | N.A.
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2223B
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 28 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE - TOP MOUNTED)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2223B
|  | 2 | Service | [8 empty] | LP FLARE K.O. DRUM AND CLOSED DRAIN DRUM SUMP
|  | 3 | Location | [8 empty] | SU-2201
|  | 4 | Mounting Type | [8 empty] | Internal
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0017
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 979.6 Kg/m3 |  |  |  |  | 1.85 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 5.5 barg |  |  |  |  | 0.5 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 60 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.45 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | N.A.
|  | 14 | Body/Cage Rating | [8 empty] | N.A.
|  | 15 | Connection Size & Location | [8 empty] | N.A.
|  | 16 | - | [8 empty] | N.A.
|  | 17 | Flange Material | [8 empty] | N.A.
|  | 18 | Length of Center To Center | [8 empty] | N.A.
|  | 19 | Case Mounting | [8 empty] | N.A.
|  | 20 | Rotatable Head | [8 empty] | N.A.
|  | 21 | Orientation | [8 empty] | N.A.
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Top Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | N.A.
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2251
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 29 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2251
|  | 2 | Service | [8 empty] | LP Flare K.O. Drum
|  | 3 | Location | [8 empty] | V-2201
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3)
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 844.4 Kg/m3 |  |  |  |  | 1.46 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 5.5 barg |  |  |  |  | 0.5 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 32 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.73 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | C.S.
|  | 14 | Body/Cage Rating | [8 empty] | 300#
|  | 15 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 16 | - | [8 empty] | -
|  | 17 | Flange Material | [8 empty] | C.S.
|  | 18 | Length of Center To Center | [8 empty] | 813 mm (32") (Note1)
|  | 19 | Case Mounting | [8 empty] | VTA
|  | 20 | Rotatable Head | [8 empty] | Yes
|  | 21 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Side Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2252A
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 30 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2252A
|  | 2 | Service | [8 empty] | LP Flare K.O. Drum
|  | 3 | Location | [8 empty] | V-2201
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0020-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 844.4 Kg/m3 |  |  |  |  | 1.46 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/7.5 barg |  |  |  |  | 0.5 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 32 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.73 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 356 mm (14")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-250 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2252B
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 31 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2252B
|  | 2 | Service | [8 empty] | LP Flare K.O. Drum
|  | 3 | Location | [8 empty] | V-2201
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0020-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 844.4 Kg/m3 |  |  |  |  | 1.46 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/7.5 barg |  |  |  |  | 0.5 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 32 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.73 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 356 mm (14")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-250 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2252C
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 32 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2252C
|  | 2 | Service | [8 empty] | LP Flare K.O. Drum
|  | 3 | Location | [8 empty] | V-2201
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0020-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 844.4 Kg/m3 |  |  |  |  | 1.46 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/7.5 barg |  |  |  |  | 0.5 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 32 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.73 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 356 mm (14")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-250 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2253
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 33 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2253
|  | 2 | Service | [8 empty] | LP Flare K.O. Drum
|  | 3 | Location | [8 empty] | V-2201
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0020-D04 (2 of 3)
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 844.4 Kg/m3 |  |  |  |  | 1.46 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/7.5 barg |  |  |  |  | 0.5 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 32 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.73 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 356 mm (14")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-250 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator | [8 empty] | Digital LCD |  |  |  |  | Yes
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2273
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 34 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE - TOP MOUNTED)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2273
|  | 2 | Service | [8 empty] | Oily Water Sump
|  | 3 | Location | [8 empty] | SU-2202
|  | 4 | Mounting Type | [8 empty] | Internal
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0021
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | OIL |  | HC
|  | 8 | Lower Liquid | [8 empty] | WATER |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 1166 Kg/m3 |  |  |  |  | 850.2 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | ATM+FULL OF WATER |  |  |  |  | ATM
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | AMB
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.61 cp |  |  |  |  | 9.69 cp
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | N.A.
|  | 14 | Body/Cage Rating | [8 empty] | N.A.
|  | 15 | Connection Size & Location | [8 empty] | N.A.
|  | 16 | - | [8 empty] | N.A.
|  | 17 | Flange Material | [8 empty] | N.A.
|  | 18 | Length of Center To Center | [8 empty] | N.A.
|  | 19 | Case Mounting | [8 empty] | N.A.
|  | 20 | Rotatable Head | [8 empty] | N.A.
|  | 21 | Orientation | [8 empty] | N.A.
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | N/A
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Top Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | N.A.
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2271
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 35 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2271
|  | 2 | Service | [8 empty] | Fuel Gas K.O. Drum
|  | 3 | Location | [8 empty] | V-2205
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0022-D04
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 48 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 813 mm (32")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-700 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.

## LIT-2272
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 36 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2272
|  | 2 | Service | [8 empty] | Fuel Gas K.O. Drum
|  | 3 | Location | [8 empty] | V-2205
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0022-D04
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Fuel Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 842.7 Kg/m3 |  |  |  |  | 5.77 Kg/m3
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | F.V/9 barg |  |  |  |  | 4.9 barg
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 48 °C
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.69 cp |  |  |  |  | 0.01 cp
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 1219 mm (48")
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Torque Tube Type | [8 empty] | Yes
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Calibration Range | [8 empty] | 0-1100 mm
|  | 37 | Ingress Protection | [8 empty] | IP65
|  | 38 | Mounting Location | [8 empty] | Side Mounted
|  | 39 | Connection Size & Location | [8 empty] | VTA
|  | 40 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 41 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 42 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 43 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD |  |  |  |  | No
|  | 44 | Zero/Span Adjusment | [8 empty] | Required
|  | 45 | Termination Type | [8 empty] | Screw terminal
|  | 46 | Case Material | [8 empty] | Low copper die-cast aluminum(VTC)
OPTIONS |  | 47 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 48 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 49 | - | [8 empty] | -
|  | 50 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 51 | Manufacturer | [8 empty] | Will be finalized later
|  | 52 | Model | [8 empty] | Will be finalized later
Notes:
VTA: Vendor to advice
1- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
D01

## LIT-2281
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 37 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2281
|  | 2 | Service | [8 empty] | Diesel Oil Drum
|  | 3 | Location | [8 empty] | V-2206
|  | 4 | Mounting Type | [8 empty] | External
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | 7 | RFI Protection |  |  |  |  | Tropicalisation |  |  |  | NEEDED |  |  |  |  | NEEDED
PROCESS CONDITIONS |  | 8 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 9 | Lower Liquid | [8 empty] | Hydrocarbon Drain |  | WATER
|  | 10 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 860 Kg/m3 |  |  |  |  | 1.46
|  | 11 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | ATM+FULL OF WATER |  |  |  |  | ATM
|  | 12 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | AMB
|  | 13 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 0.06 |  |  |  |  | 0.01
BODY / GAGE |  | 14 | Body/Cage Material | [8 empty] | C.S.
|  | 15 | Body/Cage Rating | [8 empty] | 300#
|  | 16 | Connection Size & Location | [8 empty] | 2" , ANSI Flange, 300#RF side
|  | 17 | - | [8 empty] | -
|  | 18 | Flange Material | [8 empty] | C.S.
|  | 19 | Length of Center To Center | [8 empty] | 2134 mm (84”) (Note1)
|  | 20 | Case Mounting | [8 empty] | VTA
|  | 21 | Rotatable Head | [8 empty] | Yes
|  | 22 | Orientation | [8 empty] | Side, Side with vent/drain connection
|  | 23 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 24 | Sensor Type | [8 empty] | Displacer
|  | 25 | Sensor Quantity | [8 empty] | 1
|  | 26 | Sensor Dimention | [8 empty] | VTA
|  | 27 | Selected Standard Span | [8 empty] | VTA
|  | 28 | Insertion Depth | [8 empty] | N/A
|  | 29 | Displacer Extension Material | [8 empty] | N/A
|  | 30 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 31 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 32 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 33 | Function | [8 empty] | Level Transmitter
|  | 34 | Output | [8 empty] | 4~20 mA, HART
|  | 35 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 36 | Ingress Protection | [8 empty] | IP65
|  | 37 | Mounting Location | [8 empty] | Side Mounted
|  | 38 | Connection Size & Location | [8 empty] | VTA
|  | 39 | Ex Protection | [8 empty] | Zone 2, EEx ia IIB T4
|  | 40 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 41 | Accuracy | [8 empty] | ±0.1% of calibrated span
|  | 42 | Integral Indicator |  |  |  |  | Write Protection |  |  |  | Digital LCD
|  | 43 | Zero/Span Adjusment | [8 empty] | VTA
|  | 44 | Termination Type | [8 empty] | Screw terminal
|  | 45 | Case Material | [8 empty] | VTA
OPTIONS |  | 46 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 47 | Vent/Drain Connection | [8 empty] | 3/4" NPT -with 3/4" isolation valve
|  | 48 | Compliance Code | [8 empty] | -
|  | 49 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 50 | Manufacturer | [8 empty] | VTA
|  | 51 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01

## LIT-2293
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DISPLACER LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 38 از 38
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0006 |  | D01
DATA SHEETS FOR LEVEL TRANSMITTER (DISPLACER TYPE - TOP MOUNTED)
GENERAL |  | 1 | Tag Number | [8 empty] | LIT-2293
|  | 2 | Service | [8 empty] | Glycol Sump Drum
|  | 3 | Location | [8 empty] | V-2107
|  | 4 | Mounting Type | [8 empty] | Internal
|  | 5 | Application | [8 empty] | Level Control
|  | 6 | P&ID No. | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0025
PROCESS CONDITIONS |  | 7 | Upper Liquid | [8 empty] | Process Gas |  | HC
|  | 8 | Lower Liquid | [8 empty] | TEG |  | WATER
|  | 9 | Density Lower | Density Upper |  |  |  | Density Upper |  |  |  | 1115 Kg/m3 |  |  |  |  | -
|  | 10 | Design Pressure | Normal Pressure |  |  |  | Normal Pressure |  |  |  | 3.5 barg |  |  |  |  | 0.20 barg
|  | 11 | Design Temp. | Normal Temp. |  |  |  | Normal Temp. |  |  |  | 85 °C |  |  |  |  | 5/50 °C
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  | Viscosity Up |  |  |  | 85.86 cp |  |  |  |  | -
BODY / GAGE |  | 13 | Body/Cage Material | [8 empty] | N.A.
|  | 14 | Body/Cage Rating | [8 empty] | N.A.
|  | 15 | Connection Size & Location | [8 empty] | N.A.
|  | 16 | - | [8 empty] | N.A.
|  | 17 | Flange Material | [8 empty] | N.A.
|  | 18 | Length of Center To Center | [8 empty] | N.A.
|  | 19 | Case Mounting | [8 empty] | N.A.
|  | 20 | Rotatable Head | [8 empty] | N.A.
|  | 21 | Orientation | [8 empty] | N.A.
|  | 22 | Cooling Extension | [8 empty] | N.A.
DISPLACER |  | 23 | Sensor Type | [8 empty] | Displacer
|  | 24 | Sensor Quantity | [8 empty] | 1
|  | 25 | Sensor Dimention | [8 empty] | VTA
|  | 26 | Selected Standard Span | [8 empty] | VTA
|  | 27 | Insertion Depth | [8 empty] | 813 mm (32") (Note1)
|  | 28 | Displacer Extension Material | [8 empty] | N/A
|  | 29 | Displacer or Float Material | [8 empty] | S.S. 316L
|  | 30 | Spring Material |  |  |  |  | Torque Tube Mtrl. |  |  |  | VTA |  |  |  |  | Inconel
|  | 31 | Trim Material | [8 empty] | S.S. 316L
TRANSMITTER |  | 32 | Function | [8 empty] | Level Transmitter
|  | 33 | Output | [8 empty] | 4~20 mA, HART
|  | 34 | Set Range |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  |  | 100%
|  | 35 | Ingress Protection | [8 empty] | IP65
|  | 36 | Mounting Location | [8 empty] | Top Mounted
|  | 37 | Connection Size & Location | [8 empty] | VTA
|  | 38 | Ex Protection | [8 empty] | Zone 1, EEx ia IIB T4
|  | 39 | Power Supply |  |  |  |  | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  |  | M20x1.5
|  | 40 | Accuracy | [8 empty] | 0.5% of full scale
|  | 41 | Integral Indicator | [8 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [8 empty] | VTA
|  | 43 | Termination Type | [8 empty] | Screw terminal
|  | 44 | Case Material | [8 empty] | VTA
OPTIONS |  | 45 | Cable Gland | [8 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [8 empty] | N.A.
|  | 47 | Compliance Code | [8 empty] | -
|  | 48 | Custom Tag | [8 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [8 empty] | VTA
|  | 50 | Model | [8 empty] | VTA
Notes:
VTA: Vendor to advice
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
2- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the displacer diameter for internal type displacer.
Deleted
D01