## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1171 |  |  | Transmital Date: 19/Jul/2022
Document Title: HVAC Calculation Note For Control Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-1171 |  |  | Transmital Date: 19/Jul/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-CN-0001-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پیرو نامه 01/2294/27253 مورخ 1401/01/28 این امور مجددا یادآور می‌شود دمای حباب تر گرفته شده (34درجه سانتیگراد) غیرواقعی بوده و لازم است دمای حباب تر و ارتفاع از سطح دریا و مقدار رطوبت مطابق نشریه 271سازمان مدیریت و برنامه ریزی کشور اصلاح و محاسبات مجددا تکرار گردد. |  | 01/2294/172242 | 1401/05/19 | محاسبات با توجه به داده های موجود در نشریه 271 سازمان مدیریت و برنامه ریزی کشور اصلاح گردید.
2 | لازم است قبل از پیوست فایل محاسبات، بخش Equipment Selection به مدرک فوق اضافه گردد. |  | 01/2294/172242 | 1401/05/19 | این به مدرک محاسبات اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H.ADINEH | Signature | M.FAKHARIAN
| Date: |  |  |  |  | Date: 05/NOV/2022