## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0016 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1339 |  |  | Transmital Date: 29/AGU/2022
Document Title: Standard Drawing For Valve Box |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-CV-TR-1339 |  |  | Transmital Date: 29/AGU/2022
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0016-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پاسخ ردیف 3 از Clarification By EPC Contractor مربوط به نقطه نظرات بخش مکانیک مورد تایید نیست. بنابراین سایز 12 اینچ درج شده در شیت 1 از 2، از نقشه Valve box حذف گردد. |  | 1401-2294-220426 | 1401/06/20 | اعمال شد
2 | استفاده از مصالح Sand Cement Grout برای آب بندی سازه مورد تایید نیست. مقتضی است به مصالح Sealant غیر حلال نفتی اشاره گردد. |  | 1401-2294-220426 | 1401/06/20 | اعمال شد
3 | در نقشه ها درصد تراکم کوبیده شده به 95 درصد اصلاح گردد. این موضوع قبلا نیز به اطلاع پیمانکار رسیده اما لحاظ نگردیده، بنابراین بازنگری و اصلاح گردد. |  | 1401-2294-220426 | 1401/06/20 | اعمال شد
4 | اتصال Concrete Block به فونداسیون کف با تعبیه ریشه گذاری آرماتور پیشنهاد می شود. ارائه طرح بهینه مورد انتظار می باشد |  | 1401-2294-220426 | 1401/06/20 | اعمال شد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: