## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0030_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1514 |  |  | Transmital Date: 19/Oct/2022
Document Title: Mechanical Data Sheets For Fire Water Main Pumps - Diesel Engine Driven |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0109-ME-TR-1514 |  |  | Transmital Date: 19/Oct/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0030_D03 |  |  | CRS Status:
item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| اطلاعات مربوط به اختلاف فشار پمپ با آخرین ویرایش مدرک محاسبات هیدرولیک و P&ID مربوطه تطابق ندارد. |  | 01/2294/329849 | 1401/09/05 | اختلاف فشار پمپ مطابق با آخرین ویرایش مدرک محاسبات و همچنین P&ID مربوطه 10.3bar درج شده است.
1 | کلاس فلنج ورودی و خروجی پمپ اصلاح گردد. |  | 01/2294/329849 | 1401/09/05 | با توجه به مقدار MAWP پمپ، کلاس فلنج های ورودی و خروجی پمپ می بایست #300,RF (معادل #250,FF) باشد که در ویرایش D04 اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
Date: 12/10/2022