## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0030_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1514 |  |  | Transmital Date: 19/Oct/2022
Document Title: Mechanical Data Sheets For Fire Water Main Pumps - Diesel Engine Driven |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0108-ME-TR-1514 |  |  | Transmital Date: 19/Oct/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-DT-0030_D03 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به كلاس خط - #150 - ، كلاس فلنج ها به #250 تغيير داده شود. |  | BK-SUR-ENG-MEC-01-06042 | 2022-10-31 | با توجه به دریافت پیشنهادات سازندگان و مقدار MAWP کلاس فلنج های ورودی و خروجی پمپ به #300 (معادل #250) اصلاح گردید.
Electrical comments :
1 | مدرك Specification For Electrical Requirements of Packaged Units بعنوان رفرنس اضافه گردد. |  | BK-SUR-ENG-MEC-01-06042 | 2022-10-31 | این مدرک پیوست MR بوده که برای سازندگان ارسال می گردد و سازنده موظف به پیروی نمودن از آن است لذا لزومی به اضافه نمودن این مدرک به عنوان رفرنس در مدرک مکانیکال نمی باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: 10/31/2022 |  |  |  |  | Date: 12/10/2022