## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DT-0006_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1587 |  |  | Transmital Date: 14 Nov 2022
Document Title: Data Sheets For Control/Regulator valves - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1587 |  |  | Transmital Date: 14 Nov 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-DT-0006_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Note 3 و ردیف 49 صفحات دیتا شیت مطابق Note 16 عمومی اصلاح شود. |  | 01/2294/340758 | 1401/09/12 | اصلاح شد. لازم به ذکر است حد اقل و حد اکثر فشار هوای موجود در محل مصرف کننده ، مطابق مدرک Process basis of design نوشته شده است اما سایزینگ actuator میبایست مطابق Spec شیر کنترلی برای کمترین فشار 3 بار انجام گیرد. ایتم شماره 49 و نوت ها همسانسازی شد.
2 | Note 4 صفحات دیتا شیت بصورت Finalized by vendor and Client agreement اصلاح گردد |  | 01/2294/340758 | 1401/09/12 | مطابق خواست کارفرمای محترم اصلاح شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 16 Nov 2022 |  |  |  |  | Date: