## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DT-0006_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1587 |  |  | Transmital Date: 14 Nov 2022
Document Title: Data Sheets For Control/Regulator valves - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1587 |  |  | Transmital Date: 14 Nov 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-DT-0006_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-06194 | 2022-11-16 | ملاحظه شد.
2 | Note شماره 4 با عدد Min air supply pressure در ردیف 6، مغایرت دارد. |  | BK-SUR-ENG-INS-01-06194 | 2022-11-16 | اصلاح شد.
3 | در بعضي از ديتاشيت ها همچنان متريال لوله API 5L GR.B ذكر شده است كه بايستي به A106 GR.B اصلاح گردد |  | BK-SUR-ENG-INS-01-06194 | 2022-11-16 | اصلاح شد.
4 | بر اساس اطلاعات فرآيندي وندور يا سازنده بايستي ملاحظات مربوط به cavitation و choke را بررسي و نيازمندي هاي لازم را لحاظ نمايد لازم به ذكر است كه مسئوليت تظابق شير و عملگرهاي انتخاب شده بر اساس نيازمندي هاي پروژه و توصيه هاي وندور بر عهده پيمانكار باشد. |  | BK-SUR-ENG-INS-01-06194 | 2022-11-16 | ملاحظه شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 16 Nov 2022 |  |  |  |  | Date: