## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-CN-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1216 |  |  | Transmital Date: 7/30/2022
Document Title: Calculation Note For Control Valve Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1216 |  |  | Transmital Date: 7/30/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-CN-0006_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پارامتر Maximum Capacity Cv برای شیرهای FCV-2101 و FCV-2102 در محاسبات پیوست با مقادیر مندرج در جدول 1-5 جدول مطابقت نداشته وباید اصلاح گردد. |  | 1401-2294-219114 | 1401/06/20 | طبق آخرین توافقات، ضمن انجام محاسبات با نرم افزار فیشر اصلاحات لازم در مدرک اعمال گردیده است.
2 | سایز خط جریان ورودی به شیر PCV-2211 بر اساس آخرین P&ID باید اصلاح گردد. |  | 1401-2294-219114 | 1401/06/20 | طبق آخرین توافقات، ضمن انجام محاسبات با نرم افزار فیشر اصلاحات لازم در مدرک اعمال گردیده است.
3 | بنابر پاسخ پیمانکار در بند سوم داده برگ پاسخ به نظرات این امور مبنی بر اینکه تعیین شیر مناسب و تایید محاسبات توسط سازنده انجام خواهد شد به اطلاع می رساند محاسبات Cv بر مبنای Normal Operating Flow مورد تایید می باشد لیکن نظرات این امور در خصوص شیر انتخاب شده و Maximum Capacity Cv بعد از دریافت داده برگ های سازنده اعلام خواهد شد. |  | 1401-2294-219114 | 1401/06/20 | مورد تایید است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: