## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-BD-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1053 |  |  | Transmital Date: 6/11/2022
Document Title: ESD Block Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1053 |  |  | Transmital Date: 6/11/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-BD-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در توضیحات Effect مندرج با عنوان Process Emergency Shut down (With ddepressurizing) مربوط به دیاگرام ESD 1A ، عبارت Train B&C اضافه گردد. |  | 1401-2294-255985 | 1401/07/18 | اعمال گردید
2 | بنا بر آخرین مدرک P&ID ارسالی، Sump Pump Trip از Effect های مربوط به ESD1 است که باید در دیاگرام درج گردد. |  | 1401-2294-255985 | 1401/07/18 | طی برگزاری جلسات Hazop این Effect به سطح 1A منتقل شده و اصلاحات لازم در این مورد و نیز نقشه های P&ID اعمال گردیده است.
3 | "instrument Air Header Pressure Low Low" می بایست در ESD1A قرار گیرد. |  | 1401-2294-255985 | 1401/07/18 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021