## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-PR-PH-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0921 |  |  | Transmital Date: 09.May.2022
Document Title: ESD Philosophy |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-0921 |  |  | Transmital Date: 09.May.2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-PR-PH-0005_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لازم است در بند 5 تعداد ESD ذکر شده تصحیح گردد. |  | 01/2294/100891 | 1401/03/23 | اصلاح گردید.
2 | لازم است پاراگراف اول بند 5،1 به ESD Level-0 تصحیح گردد. |  | 01/2294/100891 | 1401/03/23 | اصلاح گردید.
3 | لازم است یکپارچگی طراحی بین ادوات جدید و موجود در نظر گرفته شود. |  | 01/2294/100891 | 1401/03/23 | مطابق بررسی های انجام گرفته درجلسات Hazop قرار بر عملکرد مستقل سایت جدید و سایت موجود میباشد. تنها هریک ازاین ایستگاهها در صورت وضعیت توقف اضطراری ایستگاه مجاور را مطلع میسازد( با ارسال status alarm)
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021