## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0002_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1490 |  |  | Transmital Date: 15-Oct-2022
Document Title: Calculation Note For Lighting System of Well Pads Switchgear Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1490 |  |  | Transmital Date: 15-Oct-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-CN-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مبنای محاسبات روشنایی، کف اتاق(اتاق صفر) می باشد، لذا محاسبات بر این اساس اصلاح شود. |  | 1401-2294-280865 | 1401-08-03 | اعمال گردید.
2 | نمودار رنگی مربوط به میزان لوکس روشنایی نیز ارائه گردد، لازم است، رنج این نمودار می بایست متناسب با حداکثر لوکس نمایش داده در هر اتاق باشد. |  | 1401-2294-280865 | 1401-08-03 | اعمال گردید.
3 | اختصاص یک عدد چراغ 1x18 w برای پشت تابلوها روشنایی یکنواختی ایجاد نمی کند، پشت تابلوها با توجه به ساختار تابلوها نی بایست بعنوان ناحیه عملیاتی محسوب شود، لازم است با افزایش چراغ روشنایی مناسب(حداقل 150 لوکس جهت کلید خانه) تامین گردد. |  | 1401-2294-280865 | 1401-08-03 | مطابق با داده برگ ارسال شده، دسترسی تابلوهای سوئیچگیر از جلو می باشد. در نتیجه در ویرایش های گذشته یک عدد چراغ 1x18 w در نظر گرفته شده بود.
4 | با توجه به طول و مساحت کلیدخانه روشنایی بصورت یکنواخت توزیع نشده است، ضروری است با افزایش چراغ در طول کلیدخانه روشنایی مناسب (حداقل 150 لوکس جهت کلید خانه) تامین گردد. |  | 1401-2294-280865 | 1401-08-03 | مطابق با نظر کارفرمای محترم تعداد چراغ و به تبع آن میزان لوکس مورد نظر به 150 لوکس افزایش پیدا کرد.
5 | محاسبات اتاق باتری با در نظر گرفتن چراغ ضد انفجار در سقف انجام گردد. |  | 1401-2294-280865 | 1401-08-03 | مطابق با ویرایش قبل مدرک ارسالی، چراغ اتاق باتری EX در نظر گرفته شده است.
6 | به جهت روشنایی یکنواخت در اطراف ترانس لازم است، در سه طرف ترانس چراغ نصب گردد. |  | 1401-2294-280865 | 1401-08-03 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.sadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 26-Oct-22 |  |  |  |  | Date: