## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-PY-0004_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1505 |  |  | Transmital Date: 17-Oct-2022
Document Title: Lighting & Small Power Layout For Switchgear Building of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1505 |  |  | Transmital Date: 17-Oct-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-PY-0004_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on following documents: -Calculation Note For Lighting System of Well Pads Switchgear Building -Architectural Drawing For Switchgear Building of Well Pads -HVAC System Layout For Switchgear Building |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | این مدرک مطابق با آخرین ویرایش مدرک معماری اصلاح گردید و در صورت هر گونه تغییر، مدارک ویرایش خواهد شد. |  |  | Will be checked later.
2 | Following documents shall be added as reference documents: -HVAC System Layout For Switchgear Building -Architectural Drawing For Switchgear Building of Well Pads -Calculation Note For Lighting System of Well Pads Switchgear Building |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | مدرک معماری ساختمان سوئیچگیر و مدرک تهویه به عنوان مرجع در نظر گرفته شد. همچنین مدرک محاسباتی روشنایی این ساختمان در مراجع قرار گرفت. |  |  | Noted and Closed.
3 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22
4 | lighting panel instalation location shall be shown. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | مطابق با ترنسمیتال 1391 جانمایی تابلو های توزیع روشنایی سوئیچگیر و محوطه بیرونی صورت پذیرفت. |  |  | Noted and Closed.
5 | Lighting fixture, outdoor installation shall be considered IP65, for other indoor installation shall be considered IP42. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | اعمال گردید. |  |  | See below item 18.
6 | It shall be clarify cable between split unit and condenser/split unit and socket will be supplied by vendor or not. (Added as note) |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | همانطور که پیشتر صحبت شد تهیه کابل ارتباطی بین کندانسور و یونیت اسپلیت بر عهده سازنده می باشد لذا در نظر گرفتن یک فیدر برای برق رسانی به کندانسور کفایت می کند. همچنین نوت 14 با این موضوع اضافه گردید. |  |  | Noted and Closed.
7 | Considered seperat sub-bus for outdoor wallmounted lighting feeder in single line diagram shall be deleted. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | طبق مذاکرات انجام شده خط صورتی در دیاگرام تک خطی تابلو روشنایی نشان دهنده سیم های مربوط به روشنایی بیرونی می باشد و منظور از آن باسبار مسی نیست. با این حال جهت رفع ابهام، این خط حذف گردید. |  |  | Noted and Closed.
8 | Lighting panel shall be considered surface mounted. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | اعمال گردید. |  |  | Noted and Closed.
9 | Incoming cable route including duct bank, size and type of conduit shall be shown. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | کاندوئیت و نحوه ورود کابل اصلی به ساختمان در مدرک "مسیر کابل" نشان داده می شود. |  |  | Noted and Closed.
10 | It shall be clarify why battery back up lighitng fixturers has not been considered in layout. Meanwhile for battery back up lighting fixturers 4 core cable or seperat wire shall be considered for battery from before switch. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | برالی داخل اتاق سوئیچگیر چراغ باتری دار در نظر گرفته شد و همچنین با توجه به اینکه باتری موجود در چراغ روشنایی توسط همان رشته سیمِ فاز تغذیه می شود لذا نیاز به در نظر گرفتن کابل 3 سیمه کفایت می کند. |  |  | Noted and Closed.
11 | Typical installation detail for each lighting equipment shall be added and specified base on "Typical Installation Details & Notes For Lighting System". |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | اعمال گردید. |  |  | See below item 19.
12 | According to basic electrical design criteria, discharge capacity for battery back up lighting fixturers shall be at least half an hour. So it shall be recheked and modified. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | مطابق با ویرایش قبل مدرک در قسمت لجند، باتری پشتیبان به صورت 30 دقیقه ذکر شده است. |  |  | Noted and Closed.
13 | There is conflict between block diagram and layout from point used JB view. If JB will be used in lighting system, so type of JB shall be modified base on location of installation. For example in battery room JB shall be Exd IIC T3, IP65, in outdoor installation shall be WP,IP55. (The legen shall be modified.) |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | اعمال گردید. |  |  | See below item 20.
14 | The location of socket in switchgear room shall be checked by considering switchgear and panel arrangement and modified. (If required) |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | اعمال گردید. |  |  | Noted and Closed.
15 | Number of lighting fixturers for diesel generator shelter has been mentioned in block diagram base on which calculation. Meanwhile type of lighting fixturers, socket and JB will be installed outdoor under shelter, so type of them (WP or not), shall be rechecked and modified. On the other hand, the related cable shall be armour type. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | با توجه به این موضوع که مکان دیزل ژنراتور نهایی نشده است در ویرایش های بعدی اعمال خواهد شد. |  |  | Will be checked later.
16 | Type of protection of lighting fixturers/switch and fan in battery room shall be Exd IIC T3, IP65. Meanwhile one socket shall be added in battery room as above mentioned electrical characteristics. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | اعمال گردید. |  |  | See below item 21.
17 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | در صورت وجود کامنت متعاقبا بررسی خواهد شد. |  |  | Noted and Closed.
18 | See above item 5: According to previous comment and telephone conversation, Lighting fixture, outdoor installation shall be considered IP65 instead of IP55 base on electrical design criteria. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | اعمال گردید.
19 | See above item 11: Typical installation detail for wall mounted lighting fixturer such as security building shall be added.. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | چراغ دیواری بیرونی (Bulk Head) به جدول جزئیات روشنایی اضافه گردید.
20 | See above item 13: IP for JB shall be added. (IP55 for outdoor and IP65 for Explosion proof type). |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | مطابق با مدرک چارچوب طراحی (Design Criteria) تمام تجهیزات روشنایی بیرونی IP65 و برای تجهیزات روشنایی داخلی IP42 در نظر گرفته شده است.
21 | See above item 16: According to previous comment and telephone conversation, type of protection "Exd IIC T3" shall be added. Meanwhile socket has not been considered. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | اعمال گردید.
22 | According to our telephone conversation, outdoor area lighting panel deleted from this document and merged in switchgear lighting panel. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | اعمال گردید.
23 | Exit lighting fixturers is always on and so shall be directly connected to related feeder. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | برق موردنظر برای این چراغ از قبل از کلید مربوطه دریافت می گردد. با این حال محل انشعاب آن اصلاح گردید.
24 | According to scope of work and NISOC comment, the cables in battery room shall be considered fire resistance. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | درنظر گرفته شد.
25 | A wall mounted lighting fixturers on the wall of tranformer room shall be added. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | چراغ دیواری بیرونی (Bulk Head) اضافه گردید.
26 | Page 2, note 8: MCB shall be modified to RCBO for Socket and Split. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | اعمال گردید.
27 | According to our telephone conversation, comment on SLD will be submitted on relevant document. |  | BK-SUR-ENG-ELE-01-06037 | 2022-10-31 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Oct-22 |  |  |  |  | Date: