## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0003_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1456 |  |  | Transmital Date: 04-Oct-2022
Document Title: Calculation Note For Lighting System of Well Pads Security Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1456 |  |  | Transmital Date: 04-Oct-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0003_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مبنای محاسبات روشنایی، کف اتاق (ارتفاع صفر) می باشد، لذا محاسبات بر این اساس اصلاح شود. |  | 1401-2294-280883 | 1401-08-03 | اعمال گردید.
2 | نمودار رنگی انتهای صفحه 8 مربوط به میزان لوکس روشنایی حداکثر تا میزان 80 لوکس را پوشش می دهد لازم است، رنج این نمودار متناسب با حداکثر لوکس نمایش داده در هر اتاق اصلاح گردد. |  | 1401-2294-280883 | 1401-08-03 | این نمودار خروجی نرم افزار بوده و مقدار لوکس تامین شده را نمایش نمی دهد و فقط میزان حداکثر روشنایی را با توجه به طیف نوری بیان می کند. همانطور که در محاسبات مشخص شده میانگین لوکس به ترتیب 338 و 251 برای اتاق های نگهبانی و استراحت می باشد.
3 | اتاق Security guard room بعنوان دفتر کار حراست محسوب می شود، لذا محاسبات روشنایی می بایست براساس office انجام شود و اختصاص یک چراغ 4x18 w مورد تایید نیست. |  | 1401-2294-280883 | 1401-08-03 | تعداد چراغ ها برای اتاق نگهبانی از یک عدد به چهار عدد افزایش یافت.
4 | روشنایی اتاق Resting area & pantry کافی نیست، یک عدد چراغ 4x18 w اضافه گردد. |  | 1401-2294-280883 | 1401-08-03 | تعداد چراغ ها برای اتاق استراحت از دو عدد به سه عدد افزایش یافت.
5 | جهت روشنایی پیاده رو اطراف ساختمان چه تمهیداتی دیده شده است. |  | 1401-2294-280883 | 1401-08-03 | چراغ های روشنایی اطراف ساختمان در نقشه Lighting & Small Power Layout for Security Building of Well Pads نمایش داده شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 18-Oct-22 |  |  |  |  | Date: