## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
SET POINT & ALARM LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 11
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0006 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
SET POINT & ALARM LIST نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | JAN.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAY.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708972
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for COMPANY Review
AB-A: As-Built –Approved

## Revisions
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
SET POINT & ALARM LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 11
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0006 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 | X | X | [6 empty] | 74
11 |  | X | [6 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
SET POINT & ALARM LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 10-
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI |  | 0006 | D01
REFERENCES:
| Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001_D02
| P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002_D05
| P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003_D05
| P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D05
| P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D05
| P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D05
| P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D05
| P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008_D05
| P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D05
| P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05
| P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011_D05
| P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D05
| P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013_D05
| P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D05
| P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D05
| P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D05
| P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017_D05
| P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018_D05
| P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019_D05
| P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020_D05
| P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021_D05
| P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D05
| P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D05
| P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024_D05
| P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D05
| P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001_D02
| P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002_D02
| P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [6 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D04
D01

## NOTES
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
SET POINT & ALARM LIST
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 11-
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0006 | D01
ABBREVIATIONS:
|  | PDIT | PRESSURE DIFFERENTIAL INDICATOR TRANSMITTER
|  | PDAH | PRESSURE DIFFERENTIAL ALARM HIGH
|  | PDAL | PRESSURE DIFFERENTIAL ALARM LOW
|  | LIT | LEVEL INDICATOR TRANSMITTER
|  | LAH | LEVEL ALARM HIGH
|  | LAHH | LEVEL ALARM HIGH HIGH
|  | LAL | LEVEL ALARM LOW
|  | LALL | LEVEL ALARM LOW LOW
|  | TIT | TEMPERATURE INDICATORTRANSMITTER
|  | TAH | TEMPERATURE ALARM HIGH
|  | TAHH | TEMPERATURE ALARM HIGH HIGH
|  | TAL | TEMPERATURE ALARM LOW
|  | FIT | FLOW INDICATOR TRANSMITTER
|  | FAH | FLOW ALARM HIGH
|  | FAL | FLOW ALARM LOW
|  | PIT | PRESSURE INDICATOR TRANSMITTER
|  | PAH | PRESSURE ALARM HIGH
|  | PAHH | PRESSURE ALARM HIGH HIGH
|  | PAL | PRESSURE ALARM LOW
|  | PALL | PRESSURE ALARM LOW LOW
NOTE:
1- Set Points will be finalized later.
2- Setpoint & alarms of the instruments that have been located in the packages, have been specified by vendor.
D01

## LIST
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
SET POINT & ALARM LIST
شماره پیمان : |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0006 | D01
IDENTIFICATION |  |  | REFERENCE | [6 empty] | SET POINT |  |  |  | UNIT | REMARKS | REVISION
ITEM | TAG NO. | DESCRIPTION | P&ID |  | LOCATION / PACKAGE NAME |  | SERVICE |  | END POINT PANEL | HH | H | L | LL
1 | FIT-2101 | Flow Transmitter | BK-GCS-PEDCO-120-PR-PI-0002 |  | GAS-111-0101-AN07-6"-PT |  | To inlet K.O. Drum (V-2105) |  | DCS | - | 7220.4 | 2297.4 | - | kg/hr | Note 1
2 | PIT -2102 |  | BK-GCS-PEDCO-120-PR-PI-0002 |  | GAS-111-0101-AN07-6"-PT |  | To inlet K.O. Drum (V-2105) |  | DCS | - | - | 5.25 | - | Barg | Note 1
3 | FIT-2102 | Flow Transmitter | BK-GCS-PEDCO-120-PR-PI-0003 |  | GAS-111-0012-AN07-8"-PT |  | To Slug Catcher (V-2104) |  | DCS | - | 12395.9 | 3944.15 | - | kg/hr | Note 1
4 | PIT -2104 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  | GAS-111-0012-AN07-8"-PT |  | To Slug Catcher (V-2104) |  | DCS |  |  | 5.25 |  | Barg | Note 1
5 | TIT-2111 | Temperature Transmiiet | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 3) |  | Slug Catcher Drum - V-2104 |  | From Gas Pig Receiver (PR-2102) |  | DCS | - | 37 | 27 | - | ᵒc | Note 1
6 | PIT-2111 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | GAS-111-0012-AN07-8"-PT |  | From Gas Pig Receiver (PR-2102) |  | ESD | 6.7 | - | - | - | Barg | Note 1
7 | PIT-2112 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | Slug Catcher Drum - V-2104 |  | V-2104 |  | DCS | - | 6.3 | 3.85 | - | Barg | Note 1
8 | PDIT-2111 | Diff. Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | Slug Catcher Drum - V-2104 |  | V-2104 |  | DCS | - | 1 | - | - | Bar | Note 1
9 | LIT-2111 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | Slug Catcher Drum - V-2104 |  | V-2104 |  | DCS | - | 3800 | 250 | - | mm | Note 1
10 | LIT-2112 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | Slug Catcher Drum - V-2104 |  | V-2104 |  | ESD | 3900 | - | - | 150 | mm | Note 1
11 | LIT-2113 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 3) |  | Degassing Vessel -V-2106 |  | From Slug Catcher Drum (V-2104) |  | DCS | - | 3530 | 500 | - | % | Note 1
12 | LIT-2114 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 3) |  | Slug Storage Tank - TK-2101 |  | To Slug Pump (P-2101 A/B) |  | DCS | - | 11300 | 800 | - | % | Note 1
13 | PIT-2113 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 3) |  | Degassing Vessel -V-2106 |  | From Slug Catcher Drum (V-2104) |  | DCS | - | 0.8 | - | - | Barg | Note 1
14 | LIT-2115 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 3) |  | Slug Storage Tank - TK-2101 |  | To Slug Pump (P-2101 A/B) |  | ESD | - | - | - | 600 | % | Note 1
15 | PIT-2114 |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0015-CN07-4"-PT |  | Close Drain Header |  | DCS | - | 20.475 | - | - | Barg | Note 1
16 | PIT-2115 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0015-CN07-4"-PT |  | Close Drain Header |  | ESD | - | - | - | 9.75 | Barg | Note 1
17 | PIT-2116A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0012-CN05-3"-PT |  | Discharge slug pump (P-2101 A) |  | ESD | 20.865 |  | - | - | Barg | Note 1
18 | PIT-2116B | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0013-CN05-3"-PT |  | Discharge slug pump (P-2101 B) |  | ESD | 20.865 | - | - | - | Barg | Note 1
19 | PIT-2114A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-111-0010-AS00-4"-NP |  | From Slug Catcher (V-2104) To slug pump (P-2101 A) |  | ESD | - | - | - | 2.875 | Barg | Note 1
20 | PIT-2114B | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-111-0011-AS00-4"-NP |  | From Slug Catcher (V-2104) To slug pump (P-2101 B) |  | ESD | - | - | - | 2.875 | Barg | Note 1
21 | TIT-2112 | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | GAS-111-0005-AN07-10"-PT |  | From Slug Catcher Drum (V-2104) |  | DCS | - | 37.97 | 26.019 | - | ᵒc | Note 1
22 | PIT-2116 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | GAS-111-0005-AN07-10"-PT |  | From Slug Catcher Drum (V-2104) |  | ESD | 6.5 | - | - | - | Barg | Note 1
23 | PIT-2117 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | Inlet Knock Out Drum - V-2105 |  | V-2105 |  | DCS | - | 5.9 | 3.57 | - | Barg | Note 1
24 | PDIT-2112 | Diff. Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | Inlet Knock Out Drum - V-2105 |  | V-2105 |  | DCS | - | 1 | - | - | Bar | Note 1
25 | LIT-2116 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | Inlet Knock Out Drum - V-2105 |  | Inlet Knock Out Drum |  | DCS | - | 640 | - | - | % | Note 1
26 | LIT-2119 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | Inlet Knock Out Drum - V-2105 |  | V-2105 |  | DCS | - | 800 | 250 | - | mm | Note 1
27 | LIT-2117 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | Inlet Knock Out Drum - V-2105 |  | V-2105 |  | ESD | 900 |  |  | - | mm | Note 1
28 | LIT-2118 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0005 |  | Inlet Knock Out Drum - V-2105 |  | V-2105 |  | ESD | 250 |  |  |  | mm | Note 1
29 | LIT-2121A | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  | V-2101A |  | V-2101-A |  | DCS | - | 950 | 500 | - | mm | Note 1
30 | LIT-2122A | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  | V-2101A |  | V-2101-A |  | ESD | 1100 | - | - | 300 | mm | Note 1
31 | PDIT-2121A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  | V-2101A |  | V-2101-A |  | DCS | - | 1 | - | - | Bar | Note 1
32 | PIT-2121A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  | GAS-111-0031A-AN05-8"-ET |  | To 1ST Stage Gas Compressor (C-2101A) |  | DCS | - | - | 3.43 | -
33 | LIT-2121B | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  | V-2101B |  | V-2101-B |  | DCS | - | 950 | 500 | - | mm | Note 1
34 | LIT-2122B | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  | V-2101B |  | V-2101-B |  | ESD | 1100 | - | - | 300 | mm | Note 1
35 | PDIT-2121B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  | V-2101B |  | V-2101-B |  | DCS | - | 1 | - | - | Bar | Note 1
36 | PIT-2121B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  | GAS-111-0031B-AN05-8"-ET |  | To 1ST Stage Gas Compressor (C-2101B) |  | DCS | - | - | 3.43 | -
37 | LIT-2121C | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  | V-2101C |  | V-2101-C |  | DCS | - | 950 | 500 | - | mm | Note 1
38 | LIT-2122C | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  | V-2101C |  | V-2101-C |  | ESD | 1100 | - | - | 300 | mm | Note 1
39 | PDIT-2121C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  | V-2101C |  | V-2101-C |  | DCS | - | 1 | - | - | Bar | Note 1
40 | PIT-2121C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  | GAS-111-0031C-AN05-8"-ET |  | To 1ST Stage Gas Compressor (C-2101C) |  | DCS | - | - | 3.43 | - |  | Note 1
41 | TIT-2121A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  | GAS-111-0031A-AN05-8"-ET |  | From 1ST Stage Gas Comp. Suction Drum (V-2101A) |  | DCS | - | 41.78 | 31.78 | - | ᵒc | Note 1
42 | PIT-2122A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  | GAS-111-0031A-AN05-8"-ET |  | From 1ST Stage Gas Comp. Suction Drum (V-2101A) |  | ESD | 6.1 | - | - | 2.45 | Barg | Note 1
43 | PIT-2125A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  | GAS-111-0036A-CN05-6"-PT |  | To 1ST Stage Air Cooler (AE-2101A) |  | ESD | 20.33 | - | - | - | Barg | Note 1
44 | TIT-2124A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  | GAS-111-0036A-CN05-6"-PT |  | To 1ST Stage Air Cooler (AE-2101A) |  | ESD | 139.8 | - | - | - | ᵒc | Note 1
45 | TIT-2121B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  | GAS-111-0031B-AN05-8"-ET |  | From 1ST Stage Gas Comp. Suction Drum (V-2101B) |  | DCS | - | 41.78 | 31.78 | - | ᵒc | Note 1
46 | PIT-2122B | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  | GAS-111-0031B-AN05-8"-ET |  | From 1ST Stage Gas Comp. Suction Drum (V-2101B) |  | ESD | 6.1 |  |  | 2.45 | Barg | Note 1
47 | PIT-2125B | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  | GAS-111-0036B-CN05-6"-PT |  | To 1ST Stage Air Cooler (AE-2101B) |  | ESD | 20.33 |  | - | - | Barg | Note 1
48 | TIT-2124B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  | GAS-111-0036B-CN05-6"-PT |  | To 1ST Stage Air Cooler (AE-2101B) |  | ESD | 139.8 | - | - | - | ᵒc | Note 1
49 | TIT-2121C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  | GAS-111-0031C-AN05-8"-ET |  | From 1ST Stage Gas Comp. Suction Drum (V-2101C) |  | DCS | - | 41.78 | 31.78 | - | ᵒc | Note 1
50 | PIT-2122C | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  | GAS-111-0031C-AN05-8"-ET |  | From 1ST Stage Gas Comp. Suction Drum (V-2101C) |  | ESD | 6.1 |  |  | 2.45 | Barg | Note 1
51 | PIT-2125C | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  | GAS-111-0036C-CN05-6"-PT |  | To 1ST Stage Air Cooler (AE-2101C) |  | ESD | 20.33 |  | - | - | Barg | Note 1
52 | TIT-2124C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  | GAS-111-0036C-CN05-6"-PT |  | To 1ST Stage Air Cooler (AE-2101C) |  | ESD | 139.8 | - | - | - | ᵒc | Note 1
53 | TIT-2126A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  | GAS-111-0037A-CS00-6"-NP |  | To 2nd stage gas comp. Suction drum (V-2102A) |  | DCS | - | 65 | 55 | - | ᵒc | Note 1
54 | TIT-2125A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  | GAS-111-0037A-CS00-6"-NP |  | To 2nd stage gas comp. Suction drum (V-2102A) |  | ESD | 75 | - | - | - | ᵒc | Note 1
55 | TIT-2126B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  | GAS-111-0037B-CS00-6"-NP |  | To 2nd stage gas comp. Suction drum (V-2102B) |  | DCS | - | 65 | 55 | - | ᵒc | Note 1
56 | TIT-2125B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  | GAS-111-0037B-CS00-6"-NP |  | To 2nd stage gas comp. Suction drum (V-2102B) |  | ESD | 75 | - | - | - | ᵒc | Note 1
57 | TIT-2126C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  | GAS-111-0037C-CS00-6"-NP |  | To 2nd stage gas comp. Suction drum (V-2102C) |  | DCS | - | 65 | 55 | - | ᵒc | Note 1
58 | TIT-2125C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  | GAS-111-0037C-CS00-6"-NP |  | To 2nd stage gas comp. Suction drum (V-2102C) |  | ESD | 75 | - | - | - | ᵒc | Note 1
59 | PDIT-2131A | Diff. Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  | V-2102A |  | V-2102A |  | DCS | - | 1 | - | - | Bar | Note 1
60 | LIT-2131A | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  | V-2102A |  | V-2102A |  | DCS | - | 950 | 500 | - | mm | Note 1
61 | LIT-2132A | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  | V-2102A |  | V-2102A |  | ESD | 1100 | 950 | - | 300 | mm | Note 1
62 | PDIT-2131B | Diff. Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  | V-2102B |  | V-2102B |  | DCS | - | 1 | - | - | Bar | Note 1
63 | LIT-2131B | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  | V-2102B |  | V-2102B |  | DCS | - | 950 | 500 | - | mm | Note 1
64 | LIT-2132B | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  | V-2102B |  | V-2102B |  | ESD | 1100 | 950 | - | 300 | mm | Note 1
65 | PDIT-2131C | Diff. Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  | V-2102C |  | V-2102C |  | DCS | - | 1 | - | - | Bar | Note 1
66 | LIT-2131C | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  | V-2102C |  | V-2102C |  | DCS | - | 950 | 500 | - | mm | Note 1
67 | LIT-2132C | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  | V-2102C |  | V-2102C |  | ESD | 1100 | 950 | - | 300 | mm | Note 1
68 | TIT-2131A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  | GAS-111-0044A-CN05-6"-ET |  | From 2ND Stage Gas Comp. Suction Drum (V-2102A) |  | DCS | - | 64.88 | 54.88 | - | ᵒc | Note 1
69 | PIT-2131A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  | GAS-111-0044A-CN05-6"-ET |  | From 2ND Stage Gas Comp. Suction Drum (V-2102A) |  | ESD | - | - | - | 9.05 | Barg | Note 1
70 | PIT-2134A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  | GAS-111-0051A-FN05-6"-IS |  | To 2ND Stage Air Cooler (AE-2102A) |  | ESD | 58.636 |  | - | - | Barg | Note 1
71 | TIT-2134A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  | GAS-111-0051A-FN05-6"-IS |  | To 2ND Stage Air Cooler (AE-2102A) |  | ESD | 157.3 | - | - | - | ᵒc | Note 1
72 | TIT-2131B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  | GAS-111-0044B-CN05-6"-ET |  | From 2ND Stage Gas Comp. Suction Drum (V-2102B) |  | DCS | - | 64.88 | 54.88 | - | ᵒc | Note 1
73 | PIT-2131B | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  | GAS-111-0044B-CN05-6"-ET |  | From 2ND Stage Gas Comp. Suction Drum (V-2102B) |  | ESD | - | - | - | 9.05 | Barg | Note 1
74 | PIT-2134B | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  | GAS-111-0051B-FN05-6"-IS |  | To 2ND Stage Air Cooler (AE-2102B) |  | ESD | 58.636 |  | - | - | Barg | Note 1
75 | TIT-2134B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  | GAS-111-0051B-FN05-6"-IS |  | To 2ND Stage Air Cooler (AE-2102B) |  | ESD | 157.3 | - | - | - | ᵒc | Note 1
76 | TIT-2131C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  | GAS-111-0044C-CN05-6"-ET |  | From 2ND Stage Gas Comp. Suction Drum (V-2102C) |  | DCS | - | 64.88 | 54.88 | - | ᵒc | Note 1
77 | PIT-2131C | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  | GAS-111-0044C-CN05-6"-ET |  | From 2ND Stage Gas Comp. Suction Drum (V-2102C) |  | ESD | - | - | - | 9.05 | Barg | Note 1
78 | PIT-2134C | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  | GAS-111-0051C-FN05-6"-IS |  | To 2ND Stage Air Cooler (AE-2102C) |  | ESD | 58.636 |  | - | - | Barg | Note 1
79 | TIT-2134C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  | GAS-111-0051C-FN05-6"-IS |  | To 2ND Stage Air Cooler (AE-2102C) |  | ESD | 157.3 | - | - | - | ᵒc | Note 1
80 | TIT-2135A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  | GAS-111-0058A-FS00-6"-NP |  | To Gas Compression Discharge Drum (V-2103) |  | DCS | - | 65 | 55 | - | ᵒc | Note 1
81 | PIT-2135A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  | GAS-111-0057A-FS00-4"-NP |  | To LP Flare Header |  | DCS | - | 56.805 | 37.87 | - | Barg | Note 1
82 | TIT-2136A | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  | GAS-111-0058A-FS00-6"-NP |  | To Gas Compression Discharge Drum (V-2103) |  | ESD | 75 | - | - | - | ᵒc | Note 1
83 | TIT-2135B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  | GAS-111-0058B-FS00-6"-NP |  | To Gas Compression Discharge Drum (V-2103) |  | DCS | - | 65 | 55 | - | ᵒc | Note 1
84 | PIT-2135B | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  | GAS-111-0057B-FS00-4"-NP |  | To LP Flare Header |  | DCS | - | 56.805 | 37.87 | - | Barg | Note 1
85 | TIT-2136B | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  | GAS-111-0058B-FS00-6"-NP |  | To Gas Compression Discharge Drum (V-2103) |  | ESD | 75 | - | - | - | ᵒc | Note 1
86 | TIT-2135C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  | GAS-111-0058C-FS00-6"-NP |  | To Gas Compression Discharge Drum (V-2103) |  | DCS | - | 65 | 55 | - | ᵒc | Note 1
87 | PIT-2135C | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  | GAS-111-0057C-FS00-4"-NP |  | To LP Flare Header |  | DCS | - | 56.805 | 37.87 | - | Barg | Note 1
88 | TIT-2136C | Temperature Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  | GAS-111-0058C-FS00-6"-NP |  | To Gas Compression Discharge Drum (V-2103) |  | ESD | 75 | - | - | - | ᵒc | Note 1
89 | PDIT-2141 | Diff. Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  | V-2103 |  | V-2103 |  | DCS | - | 1 | - | - | Bar | Note 1
90 | LIT-2141 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  | V-2103 |  | V-2103 |  | DCS | - | 950 | 500 | - | mm | Note 1
91 | PDIT-2143 | Diff. Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  | GAS-111-0366-FN05-2"-PT |  | To Dehydration Package (PK-2101) |  | DCS | - | 53 | 2 | - | Bar | Note 1
92 | LIT-2142 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  | V-2103 |  | V-2103 |  | ESD | 1100 | - | - | 300 | mm | Note 1
93 | PIT-2151 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 1) |  | PK-2101 Dehydration Package |  | To PL-3201 |  | DCS | - | 55.545 | 37.03 | - | Barg | Note 1
94 | LIT-2162 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  | TK-2102 |  | V-2103 |  | DCS | - | 4300 | 800 | - | mm | Note 1
95 | LIT-2161 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  | TK-2102 |  | V-2103 |  | ESD | - | - | - | 600 | mm | Note 1
96 | PIT-2161 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  | TK-2102 |  | V-2103 |  | DCS | - | 2.2 | 1.05 | - | Barg | Note 1
97 | PIT-2202 |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  | PLA-112-0010-AN04-1 1/2"-PT |  | To Plant Air Users |  | ESD | - | - | - | 4.5 | Barg | Note 1
98 | PIT-2201 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  | PLA-112-0010-AN04-1 1/2"-PT |  | To Plant Air Users |  | DCS | - | 9.8 | 6.3 | - | Barg | Note 1
99 | PIT-2203 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | From Air Dryer Package (PK-DR-2203) |  | DCS | - | - | 5.6 | - | Barg | Note 1
100 | PIT-2201A | Pressure Switch Low Low | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | From Air Dryer Package (PK-DR-2203) |  | ESD | - | - | - | 4 | Barg | Note 1
101 | PIT-2201B | Pressure Switch Low Low | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | From Air Dryer Package (PK-DR-2203) |  | ESD | - | - | - | 4 | Barg | Note 1
102 | PIT-2201C | Pressure Switch Low Low | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | From Air Dryer Package (PK-DR-2203) |  | ESD | - | - | - | 4 | Barg | Note 1
103 | PT-2211A | Pressure Switch Low Low | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  | Nitrogen Receiver - V-2204 |  | Nitrogen Package |  | ESD | - | - | - | 4 | Barg | Note 1
104 | PT-2211B | Pressure Switch Low Low | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  | Nitrogen Receiver - V-2204 |  | Nitrogen Package |  | ESD | - | - | - | 4 | Barg | Note 1
105 | PT-2211C | Pressure Switch Low Low | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  | Nitrogen Receiver - V-2204 |  | Nitrogen Package |  | ESD | - | - | - | 4 | Barg | Note 1
106 | PIT-2111 |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  | NIT-112-0024-AN01-2"-PT |  | Nitrogen Package |  | ESD |  |  |  | 4 | Barg | Note 1
107 | PIT-2213 |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  | NIT-112-0021-AN01-2"-PT |  | Nitrogen Package |  | DCS | - | 8.8 | 5.6 | - | Barg | Note 2
108 | LIT-2221 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | V-2202 |  | V-2202 |  | DCS | - | H1=2150 H2=2225 | 300 | - | mm | Note 1
109 | LIT-2223 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | SU-2201 |  | SU-2201 |  | DCS | - | 400 | 100 | - | mm | Note 1
110 | PIT-2222A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | CDH-112-0031-AN07-2"-PT |  | Inlet P-2202-A |  | DCS | - | - | - | 0.4 | Barg | Note 1
111 | PIT-2222B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | CDH-112-0032-AN07-2"-PT |  | Inlet P-2202-B |  | DCS | - | - | - | 0.4 | Barg | Note 1
112 | LIT-2223B | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | Closed Drain Drum - V-2202 |  | LP Flare K.O. Drum and Closed Drum |  | DCS | - | 40 | 10 | - | % | Note 1
113 | LIT-2222 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | Closed Drain Drum - V-2202 |  | Closed Drain Drum |  | ESD | - | - | - | 150 | % | Note 1
114 | LIT-2231 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  | PK-2207 |  | From Local Control Panel (PK-TK-2207) |  | DCS |  |  |  | BY VENDOR | mm | Note 1
115 | LIT-2251 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | V-2201 |  | V-2201 |  | DCS | - | H1=550 H2=600 | 250 | - | mm | Note 1
116 | LIT-2252A | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | V-2201 |  | V-2201 |  | ESD | 650 | - | - | - | mm | Note 1
117 | LIT-2252B | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | V-2201 |  | V-2201 |  | ESD | 650 | - | - | - | mm | Note 1
118 | LIT-2252C | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | V-2201 |  | V-2201 |  | ESD | 650 | - | - | - | mm | Note 1
119 | LIT-2253 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | V-2201 |  | V-2201 |  | ESD | - | - | - | 150 | mm | Note 1
120 | PIT-2251A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | CDH-112-0036-AN07-2"-PT |  | Inlet P-2201-A |  | ESD |  |  |  | 0.3 | Barg | Note 1
121 | PIT-2251B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | CDH-112-0036-AN07-2"-PT |  | Inlet P-2201-B |  | ESD |  |  |  | 0.3 | Barg | Note 1
122 | PIT-2252 |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | FL-112-0004-AN07-12"-PT |  | To LP Flare Stack (FST-2201) |  | DCS |  |  | 0.25 |  | Barg | Note 1
123 | LIT-2273 |  | BK-GCS-PEDCO-120-PR-PI-0021 |  | SU-2202 |  | SU-2202 |  | DCS | - | 2700 | - | - | mm | Note 1
124 | PIT-2272 |  | BK-GCS-PEDCO-120-PR-PI-0022 |  | FLG-112-0006-AN07-3"-PT |  | From inlet K.O. Drum (V-2105) |  | DCS | - | 5.7 | 3.43 | - | Barg | Note 1
125 | LIT-2271 |  | BK-GCS-PEDCO-120-PR-PI-0022 |  | V-2205 |  | V-2205 |  | DCS | - | 950 | 500 | - | mm | Note 1
126 | PIT-2271 |  | BK-GCS-PEDCO-120-PR-PI-0022 |  | FLG-112-0106-AN07-2"-PT |  | From inlet K.O. Drum (V-2105) |  | DCS |  |  | 3.43 |  | Barg | Note 1
127 | LIT-2272 |  | BK-GCS-PEDCO-120-PR-PI-0022 |  | V-2205 |  | V-2205 |  | ESD | 1100 | - | - | 300 | mm | Note 1
128 | LIT-2281 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 1) |  | V-2206 A |  | V-2206 A |  | DCS | 1750 |  |  | 150 | mm | Note 1
129 | LIT-2281B | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0023 (2 of 2) |  | Diesel Oil Drum- V-2206B |  | Diesel Oil Drum |  | DCS | - | 1300 | 150 | - | mm | Note 1
130 | PIT-2281A | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 1) |  | Diesel Oil Drum- V-2206 |  | Diesel Oil Drum |  | ESD | - | - | - | 0.05 | Barg | Note 1
131 | LIT-2291 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0024 (1 of 1) |  | TK-2209 |  | TK-2209 |  | DCS | - | 2250 | 150 | - | mm | Note 1
132 | LIT-2293 | Level Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0025 (1 of 1) |  | V-2107 |  | V-2107 |  | DCS | - | 650 | 300 | - | mm | Note 1
133 | PIT-2291 | Pressure Indicator Transmitter | BK-GCS-PEDCO-120-PR-PI-0025 (1 of 1) |  | V-2107 |  | V-2107 |  | DCS | - | 0.5 | - |  | Barg | Note 1
134 | LIT-2301 | Level Indicator Transmitter | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  | TK-2301-A |  | TK-2301-A |  | DCS | 8500 | 8300 | 1000 | - | mm | Note 1
135 | LIT-2302 | Level Indicator Transmitter | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  | TK-2301-B |  | TK-2301-B |  | DCS | 8500 | 8300 | 1000 | - | mm | Note 1
136 | LSLL-2301 | Level Switch Low Low | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  | TK-2301-A |  | TK-2301-A |  | F&G | - | - | - | 850 | mm | Note 1
137 | LSLL-2302 | Level Switch Low Low | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  | TK-2301-B |  | TK-2301-B |  | F&G | - | - | - | 850 | mm | Note 1
138 | PT-2301 |  | BK-GCS-PEDCO-120-SA-PI-0001 (2of 2) |  | To Fire Waer Network |  | To Fire Waer Network |  | F&G | - | - | 3 | - | Barg | Note 1
139 | PT-3201A |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  | GAS-113-0072-FN05-8"-PT |  | To Pig Receiver (PR-3201) |  | ESD |  |  |  | 25.45 | Barg | Note 1
140 | PT-3201B |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  | GAS-113-0072-FN05-8"-PT |  | To Pig Receiver (PR-3201) |  | ESD |  |  |  | 25.45 | Barg | Note 1
141 | PT-3201C |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  | GAS-113-0072-FN05-8"-PT |  | To Pig Receiver (PR-3201) |  | ESD |  |  |  | 25.45 | Barg | Note 1
D01