## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-W018S-PEDCO-110-PI-RT-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0932 |  |  | Transmital Date:11-May-2022
Document Title: PDMS Model Review Report (60%) - W018S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-PI-TR-0932 |  |  | Transmital Date:11-May-2022
[5 empty] | CRS No:CRS-BK-W018S-PEDCO-110-PI-RT-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | به چه علت انشعاب ابزاردقيق TG بصورت مورب نصب گرديده است، شفاف سازي گردد. بر اساس كامنت ابزار دقيق براي نصب، تعمير و نگهداري وضعيت نصب قائم به مراتب بهتر مي باشد. لذا محل نصب TGروي خط در مدل سه بعدي بصورت قائم نشان داده شود |  | BK-SUR-ENG-PIP-01-04376 | 2022-05-23 | در مدل 90% بررسی خواهد گردید و درصورت امکان بصورت قائم نشان داده خواهد شد.
2 | Sample Connection قبل از Stone Trap در مدل نشان داده شود. تمامي نمونه گير ها بر اساس |  | BK-SUR-ENG-PIP-01-04376 | 2022-05-23 | در مدل 90% بررسی خواهد گردید.
3 | سيني و لدر براي كابل و تيوبينگ ابزار دقيق و برق بصورت مستقل از تجهيزات واحد در نظر گرفته شده و در مدل نشان داده شود. |  | BK-SUR-ENG-PIP-01-04376 | 2022-05-23 | در مدل 90% بررسی خواهد گردید.
4 | كنترل پنل سرچاهي به همراه Shutdown Button در مدل نشان داده شود. |  | BK-SUR-ENG-PIP-01-04376 | 2022-05-23 | با توجه به صورتجلسه چاه 28 ، مقرر گردید با درنظر گرفتن مجاورت درب نفررو و کابینت WHCP و وجود شاسی مورد نظربرروی کابینت نیازی به درنظرگرفتن مجدد این شستی نمی باشد .
5 | مطابق صورتجلسه بررسي مدل سه بعدي چند راهه و موقعيت چاه W028 در خصوص موارد عمومي چاههاي بينك با توجه به اعلام موارد و نظرات مهندسي واحد بهره برداري گچساران كارفرما كه طي نامه شماره 2294/52739 اعلام شده است و از آنجا كه موارد در مدل اعمال نشده است اصلاحات بر آن اساس لحاظ گردد. |  | BK-SUR-ENG-PIP-01-04376 | 2022-05-23 | در مدل 90% بررسی خواهد گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: F.Amiri | Signature |  |  |  | Clarified By: A.Dabiri | Signature
| Date: 23-May-2022 |  |  |  |  | Date: 23-May-2022