## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0006_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1429 |  |  | Transmital Date: 21-Sep-2022
Document Title: Calculation Note For Earthing & Lightning System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0106-EL-TR-1429 |  |  | Transmital Date: 21-Sep-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0006_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | 5.4 Earth Conductor: Maximum short circuit level has been mentioned 68KA.!!! What is the reference of short circuit level? |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | سطح اتصال کوتاه شبکه 50 کیلوآمپر در نظر گرفته شده است. |  |  | Noted and Closed.
2 | 6.1 Earthing Conductor Sizing According to our telephone conversation, the reference standard and vlaue of K, shall be modified base on IEC 60363-5-54 table A.54.2. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | ضرایب جدید در محاسبات مطابق با آخرین استانداردهای موجود در نظر گرفته شده است. |  |  | Noted and Closed.
3 | 6.2 Calculation of Main Earthing Conductor at Substation: According to our telephone conversation, when short circuit current runs through ground loop, it will divide into two paths and consequently ground conductor shall tolerate only I/2=25KA. By using single core PVC insulated conductor in the switchgear building, k factor is 143 and therefore; S_min= (I √t)/k=(25000×√0.5)/143=124 A =150 mm2 (Earthing Loop at Substation) |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | ضرایب جدید در محاسبات مطابق با آخرین استانداردهای موجود در نظر گرفته شده است. |  |  | See below item 11, 12
4 | 6.3 Rod Resistance: The soil resistivity of binak area shall be modified after finalizing or minor comments on geotechnical study. Meanwhile geotechnical study has not been submitted unitll now. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | بر اساس گزارش مطالعات خاک، مقاومت ویژه جدید در محاسبات در نظر گرفته شده است. بر همین اساس مطالعات سیستم زمین به روزرسانی گردید. |  |  | Noted and Closed.
5 | 6.4 Instrument Earth: It shall be calculated and mentioned in document. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | مطالعات سیستم زمین بر اساس گزارش خاک مورد بازنگری قرار گرفته است. در صورت وجود هر گونه کامنت جدید، این مدرک مورد ویرایش قرار خواهد گرفت. |  |  | Noted and Closed.
6 | Diesel generator and related local panel will be installed outdoor under shelter, so the earth loop calculation for diesel generator shelter shall be added. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | در مدرک محاسباتی به دو جدول از استاندارد مربوط به سطح مقطع کابل ارت تجهیزات مختلف اشاره شده است. ضمن اینکه در نقشه جانمایی سیستم ارتینگ، کابلهای مورد نیاز به صورت دقیق نشان داده خواهد شد. |  |  | See below item 13
7 | Outdoor area and equivalent resistor for power grounding system shall be added to this document. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 |  |  |  | Noted and Closed.
8 | Calculation for grounding system for lightning protection system shall be added to this document. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | مطالعات صاعقه گیر همانطور که در ویرایش قبلی وجود داشت، در این مدرک مورد بازنگری قرار گرفته است. |  |  | Noted and Closed.
9 | Iran isokeraunic table shall be added to this document. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | جدول مربوط به صاعقه گیر مناطق مختلف ایران نشان داده شده است. |  |  | See below item 14
10 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | در صورت وجود کامنت، موارد در ویرایشهای بعدی لحاظ خواهد شد. |  |  | Noted and Closed.
11 | See above item 3: It shall be rechecked and modified for Earthing Conductor around Substation. |  | BK-SUR-ENG-ELE-01-05860 | 2022-10-08 | محاسبه در بخش 7.2 با توجه به وجود دو مسیر یکسان برای تخلیه جریان اتصال کوتاه به روزرسانی گردید.
12 | Re. Part 7.2, it shall be note that existing substation building already has earth loop therefor why new earth loop has been considered and sized for this building? From the technically point of view existing earth loop is required and enough; new switchgear earthing conductors shall be connected to existing earth loop. |  | BK-SUR-ENG-ELE-01-05860 | 2022-10-08 | جهت احتیاط و با توجه به احتمال فرسودگی سیستم ارت بدلیل اهمیت حفاظت پست برق، رینگ ارت جدید طراحی شده است.
13 | See above item 6: Ground Conductor Sizing for neutral conductor of Emergency Generator shall be claculated. |  | BK-SUR-ENG-ELE-01-05860 | 2022-10-08 | با توجه به اینکه سطح اتصال کوتاه ترانس از ژنراتور بیشتر است، لذا شرایط بدبیانه در نظر گرفته شده است. همچنین مطابق با نقشه Layout نقطه نوترال دیزل ارت خواهد شد.
14 | See above item 9: مقدار T_d بر اساس جدول شماره 9 نشریه "طبقه‌بندي شرایط اقلیمی و محیطی"- معاونت برنامه‌ریـزي و نظـارت راهبـردي ریاست جمهوري (معاونت امور فنی) با همکاري وزارت نیـرو- شـرکت توانیر اصلاح گردد و محاسبات مرتبط مجدداً به روز رساني گردد. |  | BK-SUR-ENG-ELE-01-05860 | 2022-10-08 | نقشه موجود در مدرک Design Basis بخش فرآیند که مورد تایید کارفرمای محترم بوده است، مورد استفاده قرار گرفته است.
15 | C3 factor shall be rechecked and modified for fire fighting shelter and related calculation shall be modified. |  | BK-SUR-ENG-ELE-01-05860 | 2022-10-08 | اصلاح گردید.
16 | According to IPS-E-EL-100(1) clause 7.11.7.2, the clean earth electrode(s) shall be located outside of resistance zone of power earthing electrode(s) (radius of this zone is generally 15 – 20 m), so the clean earth claculation (Clause 8.2) shall be rechecked and modified (if required) base on free space in GCS. |  | BK-SUR-ENG-ELE-01-05860 | 2022-10-08 | با توجه به استاندارد فاصله بین سیستم زمین برق و ابزار دقیق در نقشه Layout لحاظ شده است.
17 | Conclusion for Calculation number of rods for lightning system (Clause 9.1) shall be added and compare with the dimention of structure for rod installation. |  | BK-SUR-ENG-ELE-01-05860 | 2022-10-08 | توضیحات مربوطه در خصوص انتخاب تعداد راد سیستم صاعقه گیر اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Oct-22 |  |  |  |  | Date: