## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-PR-DT-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1466 |  |  | Transmital Date: 10/9/2022
Document Title: Process Data Sheets For Instrument Devices - W007S & Extension Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1466 |  |  | Transmital Date: 10/9/2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-PR-DT-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق مذاكرات پيشين، بخش فرآیند نقطه نظرات خود را مستقيما بر داده برگ ابزار دقيق ارائه می کند. با اين وجود و با توجه به اصرار ذينفع اصلي بر تهيه اين مدرك، نقطه نظرات بصورت اجمالي بر اين مدرك نيز ارائه مي گردد. |  | BK-SUR-ENG-PCS-01-05973 | 2022-10-25 | مورد تایید است .
2 | Location مربوط به ردیف های 22 و 23 اصلاح گردد. |  | BK-SUR-ENG-PCS-01-05973 | 2022-10-25 | اصلاح گردید.
3 | نظرات ذینفع اصلی پروژه در خصوص این مدرک، اعمال گردد. |  | BK-SUR-ENG-PCS-01-05973 | 2022-10-25 | اعمال گردید .
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021

## Diesel Oil
Tank Sizing (Vertical)
Item | Value | Unit
Height (H) | 1.5 | m
Diameter (ID) | 3.2 | m
HLL | 1.3 | m
LLL | 0.15 | m
Nominal Capacity | 12.0576 | m3
Working Capacity | 9.2442 | m3 | 9.1168
Elevation | 3.5 | m
Diesel Consumption
Usage | 21.5 | gal/hr for 300 kW
Usage | 0.0814 | m3/hr
Usage Duration | 8 | hr
Daily Usage | 0.6512 | m3
Hold-Up | 14 | day
Total Vol. | 9.1168 | m3
Note on D14: Roshanak Haditalab: Based on vendor data.
Note on D15: Roshanak Haditalab: Coverter.