## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0008 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1170 |  |  | Transmital Date: 7/19/2022
Document Title: Standard Drawing For Civil Underground Crossings |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-CV-TR-1170 |  |  | Transmital Date: 7/19/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-000-CV-DW-0008_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در NOTE نقشه اشاره شود: تعداد لوله های اسلیو داکت بنک ها - ترسیم شده در نقشه- جنبه راهنمایی داشته و تعداد دقیق آن به هنگام عملیات اجرایی و با حضور و تایید دستگاه نظارت مقیم نهایی می شود. |  | 1401-2294-156948 | 1401/05/06 | اعمال شد.
2 | جنس Pipe Sleeve به دلیل شکسته شدن در عملیات اجرایی ( بتن ریزی و ....) از PVC به HP تغییر یابند. |  | 1401-2294-156948 | 1401/05/06 | اعمال شد.
3 | مقتضی است در دیتیل داکت بانک ها شبکه آرماتور (وایرینگ) لوله های اسلیو با رعایت فاصله استاندارد نمایش داده شوند. (منظور شبکه آرماتور طولی و عمودی دربرگیرنده لوله های اسلیو است.) |  | 1401-2294-156948 | 1401/05/06 | اعمال شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: