## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1451 |  |  | Transmital Date: 03-Oct-2022
Document Title: Overall Earthing Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1451 |  |  | Transmital Date: 03-Oct-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-PY-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised as AFC after finalizing or minor comments on "Calculation Note For Earthing & Lightning System" and latest revision of "Unit Plot Plan Drawing" document. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | اعمال می گردد.
2 | According to our comment on "Calculation Note For Earthing & Lightning System" document, it shall be note that existing substation building already has earth loop. Therefore, From the technically point of view existing earth loop is required and enough; new switchgear earthing conductors shall be connected to existing earth loop via existing earth terminals or new earth terminals. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | جهت احتیاط بدلیل احتمال فرسودگی سیستم زمین موجود و نداشتن نقشه معتبر جهت اتصال سیستم جدید به سیستم قدیم لوپ ارت جدید طراحی شده است.
3 | According to our comment on "Calculation Note For Earthing & Lightning System" document, According to IPS-E-EL-100(1) clause 7.11.7.2 and telephone conversation, the clean earth electrode(s) shall be located outside of resistance zone of power earthing electrode(s) (radius of this zone is generally 15 – 20 m), so the clean earth location shall be rechecked and modified base on free space in GCS. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | اصلاح گردید.
4 | Number of earth bar is not enough in some places such as in compressor, air cooler and pipe rack area (see attached file as existing outdoor area earthing layout). Meanwhile for utility and fire water pump house shelter, it is recommended to be considered earth bar and all of earth connection, connected to earth bar and then earth bar connected to main earthing loop from two points. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | اعمال گردید. لازم به ذکر است هر کدام از دیسپاچرهای ارت تعداد 10 عدد محل اتصال دارد.
5 | It shall be clarify earthing for instrument JB will be shown in which document? |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | در نوت 12 به ارت JB های ابزاردقیق اشاره شده است.
6 | Table of minimum grounding conductor size for electrical equipment/process equipment according To IPS-D-EL-417 shall be added to layout. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | در مدرک محاسباتی جدول مربوطه وجود دارد. همچنین در برگ سوم از این مدرک اضافه گردید.
7 | Following notes shall be added: -All welding sockets, junction boxes, lighting towers/Poles, panels and other equipment shall be connected to earthing system. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | نوت 12 اضافه گردید.
8 | Note 9 shall be rechecked and modified. (Clean earth has been shown.) |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | نوت شماره 9 که اکنون به شماره 10 منتقل گردیده است، اشاره به دیتل اجرایی برای ساختمانها و شلتر دارد.
9 | Note 2: Instrument earth cable color shall be rechecked and modified. (Blue/Yellow is not acceptable) |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | جهت جداسازی دو سیستم Clean Earth و Dirty Earth، تفکیک رنگی صورت گرفته است. از اینرو Y/G مربوط به ارت برق و Y/B مربوط به ارت ابزاردقیق می باشد.
10 | Typical installation detail No. shall be added on layout base on Typical Installation Details & Notes For Earthing and Lightning Protection System. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | به دلیل تعداد زیاد نقاط اتصال به شبکه ارت و جهت جلوگیری از شلوغ شدن نقشه، از درج دیتل اجرایی صرف نظر شده است. این در حالی است که مرجع شماره 4 به استاندارد اجرایی اشاره دارد.
11 | Fence of new flare area shall be shown and noted or shown it shall be connected to existing earth loop as note 4. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | ارت فلر جدید به ارت فلر موجود متصل خواهد شد. همچنین جهت اطمینان بیشتر یک چاه ارت با دریچه بازدید در نظر گرفته شده است.
12 | with considering existing earthing layout, where ever existing loop is available it shall be used in order to reduce project cost. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | حتی المقدور از سیستم ارت موجود استفاده شده است. و در برخی موارد جهت حصول اطمینان بیشتر، شبکه ارت جدید در نظر گرفته شده است.
13 | Complementary comments will be submitted after receiving revised document. |  | BK-SUR-ENG-ELE-01-05900 | 2022-10-15 | اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 15-Oct-22 |  |  |  |  | Date: