## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0008-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1279 |  |  | Transmital Date: 16-Aug-2022
Document Title: Calculation note for diesel generator sizing of well pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1279 |  |  | Transmital Date: 16-Aug-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0008-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | According to our telephone conversation, this document shall be modified base on attached color markup document and comments on prerequisite documents such as load list. The description of colors in attached document is as below: Green Color: Modified. Red Color: Deleted. Blue Color: Added Yellow Color: Checked and modified. (If required) |  | BK-SUR-ENG-ELE-00-03005 | 2022-02-09 | از فایل نمونه استفاده گشت و موارد به شرح کامنت، اعمال گردید. |  |  | Noted and Closed.
2 | This document shall be submitted as IFA after finalizing or minor comments on prerequisite documents such as load list. |  | BK-SUR-ENG-ELE-00-03005 | 2022-02-09 | اعمال می گردد. |  |  | Will be checked later.
3 | A highlighted bold Note shall be added to this document : "Diesel Generator sizing calculation will be checked and finalized by IRP Manufacturer based on IRP motor and VFD characteristics" |  | BK-SUR-ENG-ELE-00-03005 | 2022-02-09 | اعمال می گردد. |  |  | Noted and Closed.
4 | No Comment. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30
5 | No Comment. Note: Bold words in following sentence on page 7 shall be modified. Diesel engine prime power shall be 165.5 kWm (net) / 175.7 kWm (gross) According to client letter 1401-2294-156941 dated on 1401-05-06, the coefficient of continuous diesel is 1.15, and therefore diesel sizing will be Page 7, item 5.1: 52⁰C shall be modified to 40⁰C. |  | BK-SUR-ENG-ELE-01-05528 | 2022-08-24 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 24-Aug-2022 |  |  |  |  | Date: