## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0002-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1142 |  |  | Transmital Date: 05-Jul-2022
Document Title: Single Line Diagram For LV Switchgear of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0104-EL-TR-1142 |  |  | Transmital Date: 05-Jul-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-SL-0002-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | عدد قید شده در مدرک مربوط به توان دیزل مورد تأیید نیست. پس از نهایی سازی مدرک سایزینگ دیزل می بایست توان تأیید شده در مدرک قید گردد. |  | 1401-2294-171114 | 1401-05-18 | توان دیزل ژنراتور بر اساس مدرک ویرایش دوم از مدرک BK-SSGRL-PEDCO-110-EL-CN-0008 مقدار 198.5 کیلوولت آمپر در نظر گرفته شده است.
2 | نمونه ولتاژ ژنراتور می بایست جهت نمایش ولتاژ به تابلوی ورودی ژنراتور در کلیدخانه ارسال گردد. |  | 1401-2294-171114 | 1401-05-18 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 17-Jul-2022 |  |  |  |  | Date: