## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0012_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1526 |  |  | Transmital Date: 22-Oct-2022
Document Title: Cable Route Layout for Desalting Unit |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1526 |  |  | Transmital Date: 22-Oct-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-PY-0012_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | It is recommended to use exisiting cable route for new cables according to common route in attached document. |  | BK-SUR-ENG-ELE-01-06083 | 2022-11-05 | مدرک UG Composite با عنوان مرجع در پیوست مدرک قرار گرفت.
2 | The number of power cables shall be rechecked and modified base on number of feeders in scope of work and supply. (Explanation that three feeders has been considered). |  | BK-SUR-ENG-ELE-01-06083 | 2022-11-05 | مطابق با شرح کار سه عدد فیدر در فضای Space می بایست قرار گرفته شود. ولی بنابر طراحی، پیشنهاد شده است دو عدد فیدر از فضای Space موجود بیشتر اشغال نشود. با توجه به روشنایی مورد نیاز و همچنین سیستم هواساز در این ساختمان بهتر است یک فیدر از باسبار نرمال و یک فیدر از باسبار اضطراری در نظر گرفته شود. بر همین اساس دو تابلوی نرمال و اضطراری در ساختمان تعبیه می شود که یکی از فیدرهای اضطراری برق UPS سیستم CCTV را تأمین می کند. با این طرح یکی از فیدرهای Space برای طرح توسعه آینده خالی خواهد ماند.
3 | Electrical Power & Control Cable List in Siahmakan Gas Injection has been mentioned as reference document, so the relevant cables shall be added to above mentioned cable list for next revision. |  | BK-SUR-ENG-ELE-01-06083 | 2022-11-05 | بر اساس توضیحات ارائه شده در بند بالا، تعداد دو عدد کابل نرمال و اضطراری در نظر گرفته شده است که می بایست به تابلویهای جدید متصل گردید. بنابراین لیست کابلها به روز گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 05-Nov-2022 |  |  |  |  | Date: