## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | SA | LI | 0001 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
HAZARD SOURCE LIST نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | JAN.2023 |  | IFA |  |  |  | A.Saber |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | NOV.2021 |  | IFC |  |  |  | E.Sadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-708630
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | SA | LI | 0001 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | [7 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## 1
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 3 از 4
053-073-9184 |  |  | BK |  | PPL |  | PEDCO |  | 320 |  | SA |  | LI |  | 0001 |  | D01
ITEM No. | TAG NUMBER | DESCRIPTION | PHASE | TYPE OF RELEASE | [8 empty] | IGNITION POINT('C) | MAX OPERATING CONDITION |  |  | DANGEROUS ITEM | CLASSIFICATION |  |  | TEMP | UFL | LFL | REMARK
|  |  |  | Grades of release (1) |  |  | Location (2) |  |  | Vent (3) |  |  |  | DENSITY(KG/M3) | TEMP.('C) | PRESS.(BARG) |  | GAS GROUP | CLASS | ZONE |  | VOL.%
|  |  |  | C | P | S | O | E | S | N | I | F
1 | PR-3201 | Pig Receiver | GAS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 49.20 / 44.59 | 59.5 / 59.7 | 46/45.7 | HYDROCARBON | IIB | CLASS I | Zone I (1.5) & Zone II ( 3m) | T3 | 0.1 | 0.018 | See Sections 10.6.6.1.1 and 10.6.6.2- FIG 49
2 | PL-3201 | Pig Launcher | GAS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 37.38 / 34.16 | 52.93 / 53.8 | 35.04 / 35.1 | HYDROCARBON | IIB | CLASS I | Zone I (1.5) & Zone II ( 3m) | T3 | 0.1 | 0.018 | See Sections 10.6.6.1.1 and 10.6.6.2- FIG 49
3 | - | Around all piping with valves, screwed fittings, flanges | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 37.38 / 34.16 | 52.93 / 53.8 | 35.04 / 35.1 | HYDROCARBON | IIB | CLASS I | Zone I & Zone II ( 3m) | T3 | 0.1 | 0.018 | see 14.3.2 Fig 96- API RP 505
DEFINITION:
Grades of release: | [13 empty] | Location:
"C":Continuous or is expected to occur for long periods. | [13 empty] | "O": open area; "E":Enclosed; "S": Sumped;
"P": Primary; A release that can be expected to occur periodically or occasionally during normal operation | [13 empty] | Vent:
"S":secondary: A release that is not expected to occur is likely to do so only in infrequently and for short periods. | [13 empty] | "N": Natural; "I":Inadequate; "F": Forced;

## 2
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 4
053-073-9184 |  |  | BK | PPL | PEDCO | 320 | SA | LI | 0001 | D01
|  | Gas Condensate |  | Gas Injection |  |  |  |  | IEC
Component |  | Mol % Summer | Mol % Winter | Mol % Summer | Mol % Winter | Ignition point © | Boiling point © | Flash point © | Gas Group | Temp. Class | LFL VOL% | UFL VOL%
H2S |  | 0.1176 | 0.1611 | 0.0547 | 0.0522 | 260 | -59.652 | -82.4 | IIB | T3 | 4 | 44
Nitrogen |  | 0 | 0 | 0.0031 | 0.0034 | NF | -195.8 | N/A | N/A | N/A | N/A | N/A
CO2 |  | 0.0109 | 0.0187 | 0.0318 | 0.0317 | NF | -78.552 | N/A | N/A | N/A | N/A | N/A
Methane |  | 0.0522 | 0.0972 | 0.6476 | 0.6897 | 600 | -161.525 | -188 | IIA | T1 | 5 | 15
Ethane |  | 0.1232 | 0.1798 | 0.1381 | 0.1315 | 515 | -88.6 | -135 | IIA | T1 | 3 | 12.5
Propane |  | 0.2607 | 0.2723 | 0.0774 | 0.0627 | 450 | -42.102 | -104 | IIA | T2 | 2.1 | 9.5
i-Butane |  | 0.0499 | 0.0404 | 0.0083 | 0.0058 | 460 | -11.73 | -83 | IIA | T1 | 1.8 | 8.4
n-Butane |  | 0.1248 | 0.0927 | 0.0185 | 0.0122 | 288 | -0.50199 | -60 | IIA | T3 | 1.9 | 8.5
i-Pentane |  | 0.0832 | 0.0513 | 0.007 | 0.0042 | 420 | 27.878 | -49 | IIA | T2 | 1.32 | 9.16
n-Pentane |  | 0.0423 | 0.0246 | 0.0038 | 0.0021 | 243 | 36.059 | -40 | IIA | T3 | 1.5 | 7.8
n-Hexane |  | 0.077 | 0.0383 | 0.0066 | 0.0032 | 225 | 68.73 | -26 | IIA | T3 | 1.1 | 7.5
n-Heptane |  | 0.0148 | 0.0065 | 0.002 | 0.0009 | 204 | 98.42 | -4 | IIA | T3 | 1 | 6.7
n-Octane |  | 0.0028 | 0.0011 | 0.0006 | 0.0002 | 206 | 125 | 13 | IIA | T3 | 1 | 6.5
n-Nonane |  | 0.0006 | 0.0002 | 0.0003 | 0.0001 | 205 | 151 | 31 | IIA | T3 | 0.8 | 2.9
n-Decane |  | 0.0001 | 0 | 0.0001 | 0 | 210 | 174.1 | 46 | IIA | T3 | 0.7 | 5.4
N-C11 |  | 0 | 0 | 0 | 0 | NA | 193 ~ 197 | 62 | IIA | T3 | N/A | N/A
C12+ |  | 0 | 0 | 0 | 0 | NA | NA | NA | N/A | N/A | N/A | N/A
Water (H2O) |  | 0.0399 | 0.0158 | 0.0002 | 0.0002 | NF | 100 | N/A | N/A | N/A | N/A | N/A
FLUID | [8 empty] | IIB | T3
NOTE:
1.This hazardous area schedule is prepared in accordance with API 505 & NFPA 497.
2.Electrical Apparatus subgroup and temperature class have been classified according to IEC 79, see Institute of Petroleum (IP) Model
3.All adequately vented enclosed areas are Zone 2 to the extent of the enclosed area
4.All floor drain sumps in the Hazardous area are considered to be Zone 1 below grade , with 0.5 metre radius Zone 2 above grade .
5. Due to the nature of the hydrocarbon gases and liquids processed all vents and drains in hydrocarbon service are hard piped to the appropriate
flare or drain system header Consequently these connections are deemed non-hazardous.
6. Liquids of Classes II (1) or III (1) or unclassified are normally non-hazardous on release with a small Zone 1 around roof vents and openings.
NA | Not Available |  | NF | Not Flammable |  | N/A | Not Applicable