## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تاسیسات سرچاهی و خطوط جرياني مربوط به موقعیت W007S
Hazard Source List - Extension of Binak B/C Manifold
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | SA | LI | 0001 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
Hazard Source List - Extension of Binak B/C Manifold نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | JAN.2023 |  | IFA |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | AUG.2022 |  | IFA |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | FEB.2022 |  | IFA |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | NOV.2021 |  | IFC |  |  |  | E.Sadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  |  | F0Z-708022
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تاسیسات سرچاهی و خطوط جرياني مربوط به موقعیت W007S
Hazard Source List - Extension of Binak B/C Manifold
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | SA | LI | 0001 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X |  | X |  |  |  | 67
4 | X | [7 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## 1
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تاسیسات سرچاهی و خطوط جرياني مربوط به موقعیت W007S
Hazard Source List - Extension of Binak B/C Manifold
شماره پیمان: |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 3 از 4
053-073-9184 |  |  | BK |  | W007S |  | PEDCO |  | 110 |  | SA |  | LI |  | 0001 |  | D03
ITEM No. | TAG NUMBER | DESCRIPTION | PHASE | TYPE OF RELEASE | [8 empty] | IGNITION POINT('C) | MAX OPERATING CONDITION |  |  | DANGEROUS ITEM | CLASSIFICATION |  |  | TEMP | UFL | LFL | REMARK
|  |  |  | Grades of release (1) |  |  | Location (2) |  |  | Vent (3) |  |  |  | DENSITY(KG/M3) | TEMP.('C) | PRESS.(BARG) |  | GAS GROUP | LIQUID CLASS | ZONE |  | VOL.%
|  |  |  | C | P | S | O | E | S | N | I | F
1 | - | FLANGES-W007S | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 680.38/371.22 | 80/79.5 | 43.8/17.6 | HYDROCARBON | IIB | CLASS I | zone II (0.5m) | T3 | 0.1 | 0.018 | see section 10.15 API 505
2 | - | FLANGES-W018S | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 777.78/485.66 | 75/73.8 | 43.8/18.4 | HYDROCARBON | IIB | CLASS I | zone II (0.5m) | T3 | 0.1 | 0.018 | see section 10.15 API 505
3 | - | FLANGES-W028 | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 680.38/426.43 | 80/79.8 | 43.8/21.1 | HYDROCARBON | IIB | CLASS I | zone II (0.5m) | T3 | 0.1 | 0.018 | see section 10.15 API 505
4 | - | FLANGES-W035 | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 680.38/469.77 | 80/79.6 | 43.8/24 | HYDROCARBON | IIB | CLASS I | zone II (0.5m) | T3 | 0.1 | 0.018 | see section 10.15 API 505
5 | - | FLANGES-W046S | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 680.38/475.85 | 80/79.1 | 43.8/24.4 | HYDROCARBON | IIB | CLASS I | zone II (0.5m) | T3 | 0.1 | 0.018 | see section 10.15 API 505
6 | - | FLANGES-W008N | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 777.78/463.19 | 75/74.1 | 43.8/17.3 | HYDROCARBON | IIB | CLASS I | zone II (0.5m) | T3 | 0.1 | 0.018 | see section 10.15 API 505
7 | GENERAL | ANY PIPING FITTING & CONNECTION ( INCLIUDE FLANGES/ VALVES/ AND ANY SCREWED CONNECTIONS) | LIQUID+ AQUEOUS | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | >200 | 777.78/463.19 | 75/74.1 | 43.8/17.3 | HYDROCARBON | IIB | CLASS I | zone II (0.5m) | T3 | 0.1 | 0.018 | see section 10.15 API 505
8 | - | OIL SUMP PIT | Liquid | Grades of release (1) C: C; Location (2) O: O; Location (2) S: S; Vent (3) N: N | >200 | 800 | AMB | ATM | HYDROCARBON | IIB | CLASS I | ZONE I (inside sump) ZONE II ( 3 m; H - 0.6 m; V) | T3 | -- | -- | clause 14.3.5 & Figure 101
9 | P-1701 | OIL SUMP PUMP | Liquid | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | >200 | 800 | AMB | ATM | HYDROCARBON | IIB | CLASS I | ZONE II ( 3 m; H - 0.6 m; V) | T3 | -- | -- | clause 14.3.5 & Figure 101
DEFINITION:
Grades of release: | [13 empty] | Location:
"C":Continuous or is expected to occur for long periods. | [13 empty] | "O": open area; "E":Enclosed; "S": Sumped;
"P": Primary; A release that can be expected to occur periodically or occasionally during normal operation | [13 empty] | Vent:
"S":secondary: A release that is not expected to occur is likely to do so only in infrequently and for short periods. | [13 empty] | "N": Natural; "I":Inadequate; "F": Forced;
D03

## 2
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تاسیسات سرچاهی و خطوط جرياني مربوط به موقعیت W007S
Hazard Source List - Extension of Binak B/C Manifold
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 4
053-073-9184 |  | BK | W007S | PEDCO | 110 | SA | LI | 0001 | D03
IEC
Component |  |  | Mol % W018,W008 | Mol % W007,W046,W028,W035 | Ignition point © | Boiling point © | Flash point © | Gas Group | Temp. Class | LFL VOL% | UFL VOL%
H2S |  |  | 0.0004 | 0.0003 | 260 | -59.652 | -82.4 | IIB | T3 | 4 | 44
Nitrogen |  |  | 0.0003 | 0 | NF | -195.8 | N/A | N/A | N/A | N/A | N/A
CO2 |  |  | 0.0022 | 0.0014 | NF | -78.552 | N/A | N/A | N/A | N/A | N/A
Methane |  |  | 0.0357 | 0.0222 | 600 | -161.525 | -188 | IIA | T1 | 5 | 15
Ethane |  |  | 0.0134 | 0.0077 | 515 | -88.6 | -135 | IIA | T1 | 3 | 12.5
Propane |  |  | 0.0161 | 0.0062 | 450 | -42.102 | -104 | IIA | T2 | 2.1 | 9.5
i-Butane |  |  | 0.0035 | 0.0012 | 460 | -11.73 | -83 | IIA | T1 | 1.8 | 8.4
n-Butane |  |  | 0.0114 | 0.0033 | 288 | -0.50199 | -60 | IIA | T3 | 1.9 | 8.5
i-Pentane |  |  | 0.0032 | 0.0011 | 420 | 27.878 | -49 | IIA | T2 | 1.32 | 9.16
n-Pentane |  |  | 0.003 | 0.0011 | 243 | 36.059 | -40 | IIA | T3 | 1.5 | 7.8
n-Hexane |  |  | 0.0171 | 0.0043 | 225 | 68.73 | -26 | IIA | T3 | 1.1 | 7.5
n-Heptane |  |  | 0.0155 | 0.0049 | 204 | 98.42 | -4 | IIA | T3 | 1 | 6.7
n-Octane |  |  | 0.0101 | 0.003 | 206 | 125 | 13 | IIA | T3 | 1 | 6.5
n-Nonane |  |  | 0.0131 | 0.0026 | 205 | 151 | 31 | IIA | T3 | 0.8 | 2.9
n-Decane |  |  | 0.0094 | 0.0024 | 210 | 174.1 | 46 | IIA | T3 | 0.7 | 5.4
N-C11 |  |  | 0.0079 | 0.002 | NA | 193 ~ 197 | 62 | IIA | T3 | N/A | N/A
C12+ |  |  | 0.0903 | 0.0152 | JAN.2023 | NA | NA | N/A | N/A | N/A | N/A
Water (H2O) |  |  | 0.7473 | 0.9213 | NF | 100 | N/A | N/A | N/A | N/A | N/A
FLUID | [7 empty] | IIB | T3
NOTE:
1.This hazardous area schedule is prepared in accordance with API 505 & NFPA 497.
2.Electrical Apparatus subgroup and temperature class have been classified according to IEC 79, see Institute of Petroleum (IP) Model
3.All adequately vented enclosed areas are Zone 2 to the extent of the enclosed area
4.All floor drain sumps in the Hazardous area are considered to be Zone 1 below grade , with 0.5 metre radius Zone 2 above grade .
5. Due to the nature of the hydrocarbon gases and liquids processed all vents and drains in hydrocarbon service are hard piped to the appropriate
flare or drain system header Consequently these connections are deemed non-hazardous.
6. Liquids of Classes II (1) or III (1) or unclassified are normally non-hazardous on release with a small Zone 1 around roof vents and openings.
NA | Not Available | NF | Not Flammable |  | N/A | Not Applicable