## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
ELECTRICAL POWER & CONTROL CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | EL | LI | 0002 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL POWER & CONTROL CABLE LIST - EXTENSION OF BINAK B/C MANIFOLDS نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | Jan.2023 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708035
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
ELECTRICAL POWER & CONTROL CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 000 | EL | LI | 0002 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 51
2 | X | [7 empty] | 52
3 | X | [7 empty] | 53
4 | X | [7 empty] | 54
5 | [8 empty] | 55
6 | [8 empty] | 56
7 | [8 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LEGEND
1. ELECTRICAL CABLE NUMBERING SYSTEM
XXX-XXXXX- XX 1 2 3
(1) 1ST Group (Cable Type Commodity Code):
HP: High Voltage Power Cable (20 KV & Above)
MP: Medium Voltage Power Cable (6 KV & Above)
LP: Low Voltage Power Cable (Voltage Less Than 1KV)
C: Control Cables
I: Instrument Cable
(2) 2ND Group
From Equipment
(3) 3RD Group
Consumer Description: To Equipment Which will be fed.
2. CABLE TYPE
A: CU/XLPE/LSH/PVC/SWA/PVC - N2XKYRY (LV MULTI-CORE)
B: CU/XLPE/SWA/PVC - N2XRY (LV MULTI-CORE)
C: CU/XLPE/PVC/AWA/PVC - N2XRY (LV SINGLE-CORE)
D: CU/PVC/LSH/PVC/SWA/PVC - NYKYRY (CONTROL MULTI-CORE)
E: CU/PVC/SWA/PVC - NYRY (CONTROL MULTI-CORE)
F: CU/SM/XLPE/SM/SC/PVC/LSH/PVC/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE)
G: CU/SM/XLPE/SM/SC/PVC/LSH/PVC/AWA/PVC - N2XSYKYRY (MV SINGLE-CORE)
H: CU/SM/XLPE/SM/SC/PVC/AWA/PVC - N2XSYRY (MV SINGLE-CORE)
I: CU/SM/XLPE/SM/SC/PVC/SWA/PVC - N2XSEYRY (MV MULTI-CORE)
J: CU/SM/XLPE/SM/SC/PVC/SWA/PVC - N2XSEYRY (HV MULTI-CORE)
K: CU/SM/XLPE/SM/SC/PVC/AWA/PVC - N2XSYRY (HV SINGLE-CORE)
R: CU/PVC/SC/BD/SC/PVC/LSH/PVC/SWA/PVC (RTD CABLE)
S: CU/XLPE/PVC - N2XY (LV SINGLE-CORE FLEXIBLE)
Z: FIRE RESISTANT OR MICC LIGHTING CABLE (FOR HAZARDOUS AREAS SUCH AS BATTERY ROOMS ...)
Notes:
1- Since there is only one Oil Sump Pump, therefore IRP shall be considered in related cell of motor. Items 16 & 17 of cable list shall be deleted.
2-Reference documents are as below:
Area Electrical Cable Route & Section Layout - Extension of Binak B/C Manifold (BK-W007S-PEDCO-110-EL-PY-0002)
تسهیلات
ELECTRICAL POWER & CONTROL CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
شماره صفحه: 3 از 4
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0002
D00
بسته کاری
W007S
پروژه
BK

## W007S
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  |  |  | Rating (KW) | Size (mm2) | Cable Size (SQMM) |  |  |  | Length (m) | O.D (mm) | Cable Type | Description | Route
|  |  |  | From | Gland (Source) | To | Gland (Field) |  |  | Core | Phase | N | E
01 | D00 | LP-MCC-UPS01A | 0.4 | Extension LV Switchgear in Manifold | M25 | 110 VAC UPS (Charger A) | M25 | 15 | 4×10 | 4C | 10 | 10 | - | 50 | 22.1 | B | 110VAC UPS A | 01/03
02 | D00 | LP-UPS01A-FB1A | 0.110DC | 110 VAC UPS (Charger A) | M32 | Fuse Box1-A | M32 | - | 2×25 | 2C | 25 | - | - | 30 | 25.2 | B | UPS Fuse Box A | 4
03 | D00 | LP-FB1A-BAT1A | 0.110DC | Fuse Box1-A | M32 | Battery Bank-A | M32 | - | 2×25 | 2C | 25 | - | - | 30 | 25.2 | B | UPS Battery Bank A | -
04 | D00 | LP-MCC-UPS01B | 0.4 | Extension LV Switchgear in Manifold | M25 | 110 VAC UPS (Charger B) | M25 | 15 | 4×10 | 4C | 10 | 10 | - | 50 | 22.1 | B | 110VAC UPS B | 01/03
05 | D00 | LP-UPS01B-FB1B | 0.110DC | 110 VAC UPS (Charger B) | M32 | Fuse Box1-B | M32 | - | 2×25 | 2C | 25 | - | - | 30 | 25.2 | B | UPS Fuse Box B | 4
06 | D00 | LP-FB1B-BAT1B | 0.110DC | Fuse Box1-B | M32 | Battery Bank-B | M32 | - | 2×25 | 2C | 25 | - | - | 30 | 25.2 | B | UPS Battery Bank B | -
07 | D00 | LP-MCC-UPSBypass | 0.4 | Extension LV Switchgear in Manifold | M25 | 110 VAC for Instrument (Bypass) | M25 | 8 | 4×10 | 4C | 10 | 10 | - | 50 | 22.1 | B | 110VAC UPS By Pass | 01/03
08 | D00 | LP-MCC-CH01A | 0.4 | Extension LV Switchgear in Manifold | M25 | 24 VDC for FACP (Charger A) | M25 | 1.2 | 4×4 | 4C | 4 | 4 | - | 100 | 17.7 | B | 24VDC Charger A | 01/02/05/06/07/08/09
09 | D00 | LP-CH01A-FB1A | 0.024DC | 24 VDC for FACP (Charger A) | M40 | Fuse Box 1-A | M40 | - | 2×95 | 2C | 95 | - | - | 30 | 37.8 | B | DC Charger Fuse Box A | 10
10 | D00 | LP-FB1A-BAT1A | 0.024DC | Fuse Box 1-A | M40 | Battery Bank-A | M40 | - | 2×95 | 2C | 95 | - | - | 30 | 37.8 | B | DC Charger Battery Bank A | -
11 | D00 | LP-MCC-CH01B | 0.4 | Extension LV Switchgear in Manifold | M25 | 24 VDC for FACP (Charger B) | M25 | 1.2 | 4×4 | 4C | 4 | 4 | - | 100 | 17.7 | B | 24VDC Charger B | 01/02/05/06/07/08/09
12 | D00 | LP-CH01B-FB1B | 0.024DC | 24 VDC for FACP (Charger B) | M50 | Fuse Box 1-B | M50 | - | 2×95 | 2C | 95 | - | - | 30 | 37.8 | B | DC Charger Fuse Box B | 10
13 | D00 | LP-FB1B-BAT1B | 0.024DC | Fuse Box 1-B | M40 | Battery Bank-B | M40 | - | 2×95 | 2C | 95 | - | - | 30 | 37.8 | B | DC Charger Battery Bank B | -
14 | D00 | LP-MCC-PDP01 | 0.4 | Extension LV Switchgear in Manifold | M25 | PDP-01 in Control Room | M25 | 1.184 | 4×4 | 4C | 4 | 4 | - | 100 | 17.7 | B | Non-UPS Load for Instrument | 01/02/05/06/11/12
15 | D00 | LP-MCC-P1701 | 0.4 | Extension LV Switchgear in Manifold | M40 | P-1701 | M40 | 30 | 3×35 | 3C | 35 | - | - | 300 | 36 | A | Oil Sump Pump | 01/02/05/06/07/13/14/15
16 | D00 | C-MCC-ESD | 0.4 | Extension LV Switchgear in Manifold | M20 | Oil Sump Pump | M20 | - | 3×2.5 | 3C | 2.5 | - | - | 50 | 15.3 | E | IRP--ESD for Oil Sump Pump | -
17 | D00 | C-MCC-DCS | 0.4 | Extension LV Switchgear in Manifold | M25 | Oil Sump Pump | M25 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | 23.5 | E | IRP--DCS for Oil Sump Pump | -
18 | D00 | C-MCC-LCS | 0.4 | Extension LV Switchgear in Manifold | M25 | LCS of P-1701 | M25 | - | 10×2.5 | 10C | 2.5 | - | - | 300 | 22.9 | D | LCS for Sump Oil Sump Pump | 01/02/05/06/07/13/14/15
19 | D00 | LP-UPS01-PDP02 | 0.4 | 110 VAC UPS Distribution Panel | M25 | PDP02 in Control Room | M25 | 7 | 4×10 | 4C | 10 | - | - | 30 | 22.1 | B | PDP-02 in Control Room | 01/02/05/06/11/12
20 | D00 | LP-PDP02-DCS01 | 0.23 | PDP-02 in Control Room | M20 | DCS System & Marshaling Panel | M20 | 1 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | DCS system & Marshaling Panel | by Instrument
21 | D00 | LP-PDP02-DCS02 | 0.23 | PDP-02 in Control Room | M20 | DCS System & Marshaling Panel (Redundant) | M20 | 1 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | DCS system & Marshaling Panel (Redundant) | by Instrument
22 | D00 | LP-PDP02-ESD01 | 0.23 | PDP-02 in Control Room | M20 | ESD System & Marshaling Panel | M20 | 0.7 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | ESD System & Marshaling Panel | by Instrument
23 | D00 | LP-PDP02-ESD02 | 0.23 | PDP-02 in Control Room | M20 | ESD System & Marshaling Panel (Redundant) | M20 | 0.7 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | ESD System & Marshaling Panel (Redundant) | by Instrument
24 | D00 | LP-PDP02-OPW | 0.23 | PDP-02 in Control Room | M20 | Operator Workstation Marshaling Panel | M20 | 0.6 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | Operator Workstation Marshaling Panel | by Instrument
25 | D00 | LP-PDP02-DCSW | 0.23 | PDP-02 in Control Room | M20 | DCS Engineering Workstation | M20 | 0.6 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | DCS Engineering Workstation | by Instrument
26 | D00 | LP-PDP02-ESDW | 0.23 | PDP-02 in Control Room | M20 | ESD Engineering Workstation | M20 | 0.6 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | ESD Engineering Workstation | by Instrument
27 | D00 | LP-PDP02-Print | 0.23 | PDP-02 in Control Room | M20 | Printers | M20 | 0.6 | 2×4 | 2C | 4 | - | - | 30 | 16 | B | Printers | by Instrument
28 | D00 | LP-CH01-FACP01 | 0.024 | DC Charger | M32 | FACP System | M32 | 0.6 | 2×35 | 2C | 35 | 35 | - | 50 | 25.2 | B | FACP System | 9/8/7/11/12
29 | D00 | LP-CH01-FACP02 | 0.024 | DC Charger | M32 | FACP System (Redundant) | M32 | 0.6 | 2×35 | 2C | 35 | 35 | - | 50 | 25.2 | B | FACP System (Redundant) | 9/8/7/11/12